D、MD、DF、DY卧式多级泵

安装使用说明书

长沙福斯水泵泵业有限公司

概  述

General

该系列泵系节段式多级离心泵，采用了国家推荐使用的高效节能水力模型，具有高效节能、性能范围广、运行安全平稳、低噪音、长寿命、安装维修方便等优点；通过改变泵的材质、密封形式和增加冷却系统，可输送热水、油类、腐蚀性和含磨料的介质等。

D型泵供输送不含固体颗粒、温度不高于80℃的清水或物理化学性质类似于清水的液体，适应于矿山和城市给排水工程使用。

DM型泵供输送固体颗粒含量不大于1.5%的中性矿水（粒度小于0.5毫米）及类似的其它污水，被输送介质的温度不高于80℃，适于钢铁厂、矿山排水、污水输送等场合。

DF型泵供输送温度为-20℃～105℃，不含固体颗粒，有腐蚀性的液体。

DY型泵用于输送不含固体颗粒，温度为-20℃～150℃，粘度小于120厘沲的油类和石油产品。

以上各型泵的进口允许压力均不超过0.6MPa。

The serial pump is multi-stage sectional centrifugal pump with the excellent hydraulic model, it has advantages of high-efficiency, energy-saving, wide performance range, operating safely and steadily, low noise, long life and convenience for installing and repairing etc. It can deliver heat water, oil, corrosive or wearable medium by changing material of pump.

Type D pump is used in mine and urban project for delivering clear water without solid particles or other liquids which are physically or chemically similar to clear water. The temperature of liquids are not be over 80℃.

Type DM pump is used to deliver neutral water with solid particles below 1.5% (viscosity less than 0.5mm) and other sewage. It is suitable for using in steel factory and mine etc. The temperature of liquids can not exceed 80℃.

Type DF pump is used for delivering corrosive liquids without solid particles, the temperature of liquids is -20℃～105℃.

Type DY pump is used for delivering oil and petroleum products without solid particles and viscosity below 120 centistokes , the temperature of liquids is -20℃～105℃.

The inlet pressure of all above pumps is less than 0.6Mpa.

型号意义

Nomenclature

D（DM、DF、DY）85-67×3

D — 多级卧式离心泵                Multi-stage horizontal centrifugal pump

DM — 耐磨多级离心泵              Multi-stage wearable centrifugal pump

DF —多级耐腐蚀离心泵              Multi-stage anti-corrosive centrifugal ump

DY —多级离心油泵                  Multi-stage centrifugal oil pump

85 — 泵设计点流量为85m³/h       The capacity is 85m3/h at design point

67 — 泵单级设计点扬程为67m       The single stage head is 67m at design

point

3 —泵的级数为3                     The stage number is 3 stage

100D16×3

100 — 泵进口直径为100mm        Inlet diameter of pump is 100mm

D —多级卧式离心泵                  Multi-stage horizontal centrifugal pump

16 — 泵单级设计点扬程为16m       The single stage head is 16m at design point

3 — 泵的级数为3                   The stage number is 3 stage

性能范围（设计点）

Range of performance (Design point)

流量Capacity：6.3～600m3/h

扬程Head：22.8～650m

结构特点

Construction feature

D、DM、DF、DY型泵主要由固定部分、转子部分、轴承和轴封四大部分组成。

1.定子部分：主要由进水段、中段、出水段和导叶等组成，用穿杠将各段拉紧，构成工作室。D型泵进口为水平方向，出口垂直向上；DM、 DF、DY型泵出口垂直向上，进口一般为水平方向，根据需要也可生产进出口垂直向上方向。

2.转子部分：主要由轴、叶轮、平衡盘和轴套等组成。轴将动力传递给叶轮使其工作；平衡盘用来平衡轴向力；轴上装有可更换的轴套以保护轴。

3.轴承部分：主要由轴承体、轴承和轴承压盖等组成。除85-67、155-67、600-60型泵采用滑动轴承、稀油润滑外，其余型泵均采用滚动轴承、润滑脂润滑。85-67、155-67也可采用滚动轴承结构。

4.轴封：一般采用软填料密封，主要由进水段和尾盖上的密封函体、填料、挡水圈等组成。密封腔内通有一定压力的水，起水封、水冷和润滑的作用。D型泵水封水一般来源于泵内的高压水， MD、DF、DY型泵来源于泵内的压力水或外部供水。MD、DF、DY型泵较多采用机械密封。

传动：泵通过弹性联轴器由原动机直接驱动。从原动机端看，泵为顺时针方向旋转。

Type D (MD、DF、DY) pump consists of stator, rotator, bearing and shaft seal:

1. Stator: main parts is suction casing, stage casing, discharge casing and Diffusor, they are screw up by poles to become a working house. The suction direction of type D pump is horizontal, its discharge direction is upward; the discharge direction of type MD, DF, DY pumps are upward, the suction direction is horizontal, they can be made upward according to user requirement.

2. Rotor: it is consist of shaft, impeller, balance disc, and shaft sleeve etc. shaft supplied power to impeller. The axial force is balanced by disc. The shaft sleeve is mounted on shaft to protect shaft.

3. Bearing parts: it is consist of bearing body, bearing and bearing cover etc. The bearing of type 85-67,155-67,600-60 pump is sliding bearing, lubricated by dilute oil, the other pump bearing is rolling bearing, lubricated by grease.

4. Shaft seal: it is usually adopted soft packing seal, consist of sealing house on suction casing, packing , blocking water ring, the seal house have some pressure water to cool. Lubricate and seal pump. Type D pump pressure water come from pump itself, type MD, DF, DY pump pressure water is come from pump itself or outer water, type MD, DF, DY pump usually adopt mechanical seal .

Drive

The pump is driver directly by motor through coupling. View from motor end, the rotating direction of pump is clockwise.

材  料

Material

| 零件名称 Part Name | D | ＭD | DY | DF |
| --- | --- | --- | --- | --- |
| 进水段 Suction casing | HT250 | ZGCr17Mo2-CuR | HT250或ZG230-450 | 铸钢或铸不锈钢Cast steel or Cast stainless steel |
| 中段 Stage casing | HT250 | ZGCr17Mo2-CuR | HT250或ZG230-450 | 铸钢或铸不锈钢Cast steel or cast stainless steel |
| 出水段 Discharge casing | HT250 | ZGCr17Mo2-CuR | HT250或ZG230-450 | 铸钢或铸不锈钢Cast steel or cast stainless steel |
| 叶轮 Impeller | HT250 | KmTBCr15Mo3 | HT250或ZG230-450 | 铸钢或铸不锈钢Cast steel or cast stainless steel |
| 导叶 Diffuser | HT250 | KmTBCr15Mo3 | HT250或ZG230-450 | 铸钢或铸不锈钢Cast steel or cast stainless steel |
| 轴Shaft | 45 | 45 | 45 | 不锈钢stainless steel |
| 平衡盘 Balance disc | ZQA19-4 | ZGCr17Mo2-CuR | ZQA19-4 | 铸钢或铸不锈钢Cast steel or cast stainless steel |

注：材料可根据用户要求选配

Remarks: Other materials can be used according user’s requirement.

D、DM、DF、DY型泵结构图

Type D/DM/DF/DY Pump Construction Drawing

| 1、轴承体 Bearing body | 2、进水段 Suction casing | 3、前级叶轮 Firs stage impeller | 4、平衡管 Equalizing pipe | 5、次级叶轮 Second stage impeller | 6、中段 Stage casing |
| --- | --- | --- | --- | --- | --- |
| 7、导叶 Diffuser | 8、平衡套 Balance sleeve | 9、平衡环 Balance ring | 10、平衡盘 Balance disc | 11、尾盖 End cover | 12、O型密封圈 O ring |
| 13、填料环 Packing ring | 14、轴套 Sleeve | 15、轴 Shaft | 16、出水段 Discharge casing | 17、末级导叶 Last stage diffuser | 18、导叶套 Diffuser sleeve |
| 19、密封环 Wearing | 20、首级密封环 First casing wearing | 21、拉紧螺栓 | 22、填料、机封 Packing/Mechanical seal | 23、填料、机封压盖 Packing/Mechanical seal gland |  |

| 性能参数表 Sheet of Performance Date |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 参 数 date 型 号 Type | 流量 Capacity Q | 扬程 Head H | 转速 Speed n | 轴功率 Shaft power Pa | 配带电动机 Motor |  | 效率 Eff η | 必需汽 蚀余量 NPSHr | 叶轮直径 Impeller dia. D |
|  |  |  |  |  | 功率 Power | 型 号 Type |  |  |  |
|  | m3/h | m | rpm | KW | KW |  | % | m | mm |
| 6-25×2 | 3.75 6.3 7.5 | 51 50 49 | 2950 | 1.49 1.84 2.08 | 3 | Y100L-2 | 35 46.5 48 | 2.0 2.0 2.5 | φ138 |
| 6-25×3 | 3.75 6.3 7.5 | 76.5 75 73.5 | 2950 | 2.23 2.77 3.12 | 5.5 | Y132S1-2 | 35 46.5 48 | 2.0 2.0 2.5 | φ138 |
| 6-25×4 | 3.75 6.3 7.5 | 102 100 98 | 2950 | 2.98 3.69 4.16 | 7.5 | Y132S2-2 | 35 46.5 48 | 2.0 2.0 2.5 | φ138 |
| 6-25×5 | 3.75 6.3 7.5 | 127.5 125 122.5 | 2950 | 3.73 4.61 5.20 | 7.5 | Y132S2-2 | 35 46.5 48 | 2.0 2.0 2.5 | φ138 |
| 6-25×6 | 3.75 6.3 7.5 | 153 150 147 | 2950 | 4.47 5.53 6.24 | 11 | Y160M1-2 | 35 46.5 48 | 2.0 2.0 2.5 | φ138 |
| 6-25×7 | 3.75 6.3 7.5 | 178.5 175 171.5 | 2950 | 5.22 6.45 7.28 | 11 | Y160M1-2 | 35 46.5 48 | 2.0 2.0 2.5 | φ138 |
| 6-25×8 | 3.75 6.3 7.5 | 204 200 196 | 2950 | 5.96 7.37 8.32 | 15 | Y160M2-2 | 35 46.5 48 | 2.0 2.0 2.5 | φ138 |
| 6-25×9 | 3.75 6.3 7.5 | 229.5 225 220.5 | 2950 | 6.71 8.29 9.36 | 15 | Y160M2-2 | 35 46.5 48 | 2.0 2.0 2.5 | φ138 |
| 6-25×10 | 3.75 6.3 7.5 | 255 250 245 | 2950 | 7.45 9.21 10.40 | 18.5 | Y160L-2 | 35 46.5 48 | 2.0 2.0 2.5 | φ138 |
| 6-25×11 | 3.75 6.3 7.5 | 280.5 275 269.5 | 2950 | 8.20 10.13 11.44 | 18.5 | Y160L-2 | 35 46.5 48 | 2.0 2.0 2.5 | φ138 |
| 6-25×12 | 3.75 6.3 7.5 | 306 300 294 | 2950 | 8.94 11.05 12.48 | 18.5 | Y160L-2 | 35 46.5 48 | 2.0 2.0 2.5 | φ138 |
| 6-50×2 | 3.75 6.3 7.5 | 104 100 96 | 2950 | 3.79 5.72 6.76 | 11 | Y160M1-2 | 28 30 29 | 3.0 3.0 3.5 | φ198 |
| 6-50×3 | 3.75 6.3 7.5 | 156 150 144 | 2950 | 5.69 8.58 10.1 | 15 | Y160M2-2 | 28 30 29 | 3.0 3.0 3.5 | φ198 |
| 6-50×4 | 3.75 6.3 7.5 | 208 200 192 | 2950 | 7.58 11.4 13.5 | 18.5 | Y160L-2 | 28 30 29 | 3.0 3.0 3.5 | φ198 |
| 6-50×5 | 3.75 6.3 7.5 | 260 250 240 | 2950 | 9.48 14.3 16.9 | 22 | Y180M-2 | 28 30 29 | 3.0 3.0 3.5 | φ198 |
| 6-50×6 | 3.75 6.3 7.5 | 312 300 288 | 2950 | 11.4 17.2 20.3 | 30 | Y200L1-2 | 28 30 29 | 3.0 3.0 3.5 | φ198 |
| 6-50×7 | 3.75 6.3 7.5 | 364 350 336 | 2950 | 13.3 20.0 23.7 | 30 | Y200L1-2 | 28 30 29 | 3.0 3.0 3.5 | φ198 |
| 6-50×8 | 3.75 6.3 7.5 | 416 400 384 | 2950 | 15.2 22.9 27.0 | 37 | Y200L2-2 | 28 30 29 | 3.0 3.0 3.5 | φ198 |
| 6-50×9 | 3.75 6.3 7.5 | 468 450 432 | 2950 | 17.1 25.7 30.4 | 37 | Y200L2-2 | 28 30 29 | 3.0 3.0 3.5 | φ198 |
| 6-50×10 | 3.75 6.3 7.5 | 520 500 480 | 2950 | 19.0 28.6 33.8 | 45 | Y225M-2 | 28 30 29 | 3.0 3.0 3.5 | φ198 |
| 6-50×11 | 3.75 6.3 7.5 | 572 550 528 | 2950 | 20.8 31.4 37.2 | 45 | Y225M-2 | 28 30 29 | 3.0 3.0 3.5 | φ198 |
| 6-50×12 | 3.75 6.3 7.5 | 624 600 576 | 2950 | 22.7 34.3 40.6 | 55 | Y250M-2 | 28 30 29 | 3.0 3.0 3.5 | φ198 |
| 12-25×2 | 7.5 12.5 15 | 56.4 50 46 | 2950 | 2.65 3.15 3.55 | 5.5 | Y132S1-2 | 44 54 53 | 2.0 2.0 2.5 | φ146 |
| 12-25×3 | 7.5 12.5 15 | 84.6 75 69 | 2950 | 3.93 4.73 5.32 | 7.5 | Y132S2-2 | 44 54 53 | 2.0 2.0 2.5 | φ146 |
| 12-25×4 | 7.5 12.5 15 | 112.8 100 92 | 2950 | 5.24 6.30 7.09 | 11 | Y160M1-2 | 44 54 53 | 2.0 2.0 2.5 | φ146 |
| 12-25×5 | 7.5 12.5 15 | 141 125 115 | 2950 | 6.55 7.88 8.86 | 11 | Y160M1-2 | 44 54 53 | 2.0 2.0 2.5 | φ146 |
| 12-25×6 | 7.5 12.5 15 | 169.2 150 138 | 2950 | 7.85 9.46 10.64 | 15 | Y160M2-2 | 44 54 53 | 2.0 2.0 2.5 | φ146 |
| 12-25×7 | 7.5 12.5 15 | 197.4 175 161 | 2950 | 9.16 11.0 12.41 | 15 | Y160M2-2 | 44 54 53 | 2.0 2.0 2.5 | φ146 |
| 12-25×8 | 7.5 12.5 15 | 225.6 200 184 | 2950 | 10.47 12.61 14.18 | 18.5 | Y160L-2 | 44 54 53 | 2.0 2.0 2.5 | φ146 |
| 12-25×9 | 7.5 12.5 15 | 253.8 225 207 | 2950 | 11.78 14.18 15.95 | 18.5 | Y160L-2 | 44 54 53 | 2.0 2.0 2.5 | φ146 |
| 12-25×10 | 7.5 12.5 15 | 282 250 230 | 2950 | 13.09 15.76 17.73 | 22 | Y180M-2 | 44 54 53 | 2.0 2.0 2.5 | φ146 |
| 12-25×11 | 7.5 12.5 15 | 310.2 275 253 | 2950 | 14.4 17.34 19.5 | 22 | Y180M-2 | 44 54 53 | 2.0 2.0 2.5 | φ146 |
| 12-25×12 | 7.5 12.5 15 | 338.4 300 276 | 2950 | 15.7 18.9 21.3 | 30 | Y200L1-2 | 44 54 53 | 2.0 2.0 2.5 | φ146 |
| 12-50×2 | 7.5 12.5 15 | 108 100 93 | 2950 | 5.8 7.6 8.3 | 11 | Y160M1-2 | 37.5 45 45.9 | 2.0 2.0 2.5 | φ198 |
| 12-50×3 | 7.5 12.5 15 | 162 150 139.5 | 2950 | 8.8 11.3 12.4 | 18.5 | Y160L―2 | 37.5 45 45.9 | 2.0 2.0 2.5 | φ198 |
| 12–50×4 | 7.5 12.5 15 | 216 200 186 | 2950 | 11.7 15.1 16.6 | 22 | Y180M―2 | 37.5 45 45.9 | 2.0 2.0 2.5 | φ198 |
| 12–50×5 | 7.5 12.5 15 | 270 250 232.5 | 2950 | 14.6 18.9 20.7 | 30 | Y200L1―2 | 37.5 45 45.9 | 2.0 2.0 2.5 | φ198 |
| 12–50×6 | 7.5 12.5 15 | 324 300 279 | 2950 | 17.6 22.7 24.8 | 30 | Y200L1―2 | 37.5 45 45.9 | 2.0 2.0 2.5 | φ198 |
| 12–50×7 | 7.5 12.5 15 | 378 350 325.5 | 2950 | 20.4 26.5 29.0 | 37 | Y200L2―2 | 37.5 45 45.9 | 2.0 2.0 2.5 | φ198 |
| 12–50×8 | 7.5 12.5 15 | 432 400 372 | 2950 | 23.3 30.3 33.1 | 45 | Y225M―2 | 37.5 45 45.9 | 2.0 2.0 2.5 | φ198 |
| 12–50×9 | 7.5 12.5 15 | 486 450 418.5 | 2950 | 26.3 34.0 37.3 | 45 | Y225M―2 | 37.5 45 45.9 | 2.0 2.0 2.5 | φ198 |
| 12–50×10 | 7.5 12.5 15 | 540 500 465 | 2950 | 29.2 37.8 41.4 | 55 | Y250M―2 | 37.5 45 45.9 | 2.0 2.0 2.5 | φ198 |
| 12–50×11 | 7.5 12.5 15 | 594 550 511.5 | 2950 | 32.1 41.6 45.5 | 55 | Y250M―2 | 37.5 45 45.9 | 2.0 2.0 2.5 | φ198 |
| 12–50×12 | 7.5 12.5 15 | 648 600 558 | 2950 | 35.0 45.4 50.0 | 75 | Y280S―2 | 37.5 45 45.9 | 2.0 2.0 2.5 | φ198 |
| 25-30×2 | 15 25 30 | 68 60 55 | 2950 | 5.56 6.58 7.14 | 11 | Y160M1-2 | 50 62 63 | 2.2 2.2 2.4 | φ160 |
| 25-30×3 | 15 25 30 | 102 90 82.5 | 2950 | 8.33 9.88 10.7 | 15 | Y160M2-2 | 50 62 63 | 2.2 2.2 2.4 | φ160 |
| 25-30×4 | 15 25 30 | 136 120 110 | 2950 | 11.11 13.1 14.26 | 18.5 | Y160L-2 | 50 62 63 | 2.2 2.2 2.4 | φ160 |
| 25-30×5 | 15 25 30 | 170 150 137.5 | 2950 | 13.89 16.47 17.83 | 22 | Y180M-2 | 50 62 63 | 2.2 2.2 2.4 | φ160 |
| 25-30×6 | 15 25 30 | 204 180 165 | 2950 | 16.67 19.77 21.4 | 30 | Y200L1―2 | 50 62 63 | 2.2 2.2 2.4 | φ160 |
| 25-30×7 | 15 25 30 | 238 210 192.5 | 2950 | 19.44 23.1 24.96 | 30 | Y200L1―2 | 50 62 63 | 2.2 2.2 2.4 | φ160 |
| 25-30×8 | 15 25 30 | 272 240 220 | 2950 | 22.22 26.4 28.53 | 37 | Y200L2―2 | 50 62 63 | 2.2 2.2 2.4 | φ160 |
| 25-30×9 | 15 25 30 | 306 270 247.5 | 2950 | 25.0 29.65 32.1 | 37 | Y200L2―2 | 50 62 63 | 2.2 2.2 2.4 | φ160 |
| 25-30×10 | 15 25 30 | 340 300 275 | 2950 | 27.8 32.9 35.7 | 45 | Y225M―2 | 50 62 63 | 2.2 2.2 2.4 | φ160 |
| 25–50×3 | 15 25 28 | 154.5 150 144 | 2950 | 14.3 18.9 20.3 | 30 | Y200L1―2 | 44 54 54 | 2.4 2.7 2.8 | φ196 |
| 25–50×4 | 15 25 28 | 206 200 192 | 2950 | 19.1 25.2 27.1 | 30 | Y200L1―2 | 44 54 54 | 2.4 2.7 2.8 | φ196 |
| 25–50×5 | 15 25 28 | 257.5 250 240 | 2950 | 23.9 31.5 33.9 | 37 | Y200L2―2 | 44 54 54 | 2.4 2.7 2.8 | φ196 |
| 25–50×6 | 15 25 28 | 309 300 288 | 2950 | 28.6 37.8 40.7 | 45 | Y225M―2 | 44 54 54 | 2.4 2.7 2.8 | φ196 |
| 25–50×7 | 15 25 28 | 360.5 350 336 | 2950 | 33.4 44.1 47.5 | 55 | Y250M―2 | 44 54 54 | 2.4 2.7 2.8 | φ196 |
| 25–50×8 | 15 25 28 | 412 400 384 | 2950 | 38.2 50.4 54.2 | 75 | Y280S―2 | 44 54 54 | 2.4 2.7 2.8 | φ196 |
| 25–50×9 | 15 25 28 | 463.6 450 432 | 2950 | 43.0 56.7 61.0 | 75 | Y280S―2 | 44 54 54 | 2.4 2.7 2.8 | φ196 |
| 25–50×10 | 15 25 28 | 515 500 480 | 2950 | 47.7 63.0 67.8 | 75 | Y280S―2 | 44 54 54 | 2.4 2.7 2.8 | φ196 |
| 25–50×11 | 15 25 28 | 566 550 528 | 2950 | 52.5 69.3 74.6 | 90 | Y280M―2 | 44 54 54 | 2.4 2.7 2.8 | φ196 |
| 25–50×12 | 15 25 28 | 618 600 576 | 2950 | 57.6 75.6 81.4 | 110 | Y315S―2 | 44 54 54 | 2.4 2.7 2.8 | φ196 |
| 46–30×2 | 30 46 55 | 68 60 54 | 2950 | 8.68 10.74 11.89 | 15 | Y160M2-2 | 64 70 68 | 2.4 2.8 4.6 | φ162 |
| 46–30×3 | 30 46 55 | 102 90 81 | 2950 | 13.02 16.11 17.84 | 22 | Y180M-2 | 64 70 68 | 2.4 2.8 4.6 | φ162 |
| 46–30×4 | 30 46 55 | 136 120 108 | 2950 | 17.36 21.48 23.79 | 30 | Y200L1―2 | 64 70 68 | 2.4 2.8 4.6 | φ162 |
| 46–30×5 | 30 46 55 | 170 150 135 | 2950 | 21.7 26.85 29.74 | 37 | Y200L2―2 | 64 70 68 | 2.4 2.8 4.6 | φ162 |
| 46–30×6 | 30 46 55 | 204 180 162 | 2950 | 26.04 32.21 35.68 | 37 | Y200L2―2 | 64 70 68 | 2.4 2.8 4.6 | φ162 |
| 46–30×7 | 30 46 55 | 238 210 189 | 2950 | 30.38 37.58 41.63 | 45 | Y225M―2 | 64 70 68 | 2.4 2.8 4.6 | φ162 |
| 46–30×8 | 30 46 55 | 272 240 216 | 2950 | 34.72 42.95 47.58 | 55 | Y250M―2 | 64 70 68 | 2.4 2.8 4.6 | φ162 |
| 46–30×9 | 30 46 55 | 306 270 243 | 2950 | 39.06 48.32 53.53 | 55 | Y250M―2 | 64 70 68 | 2.4 2.8 4.6 | φ162 |
| 46–30×10 | 30 46 55 | 340 300 270 | 2950 | 43.4 53.69 59.47 | 75 | Y280S―2 | 64 70 68 | 2.4 2.8 4.6 | φ162 |
| 46–50×2 | 30 46 55 | 111 100 92 | 2950 | 16.78 19.88 21.52 | 30 | Y200L1―2 | 54 63 64 | 2.5 2.8 3.2 | φ210 |
| 46–50×3 | 30 46 55 | 166.5 150 138 | 2950 | 25.19 29.83 32.28 | 37 | Y200L2―2 | 54 63 64 | 2.5 2.8 3.2 | φ210 |
| 46–50×4 | 30 46 55 | 222 200 184 | 2950 | 33.59 39.77 43.04 | 45 | Y225M―2 | 54 63 64 | 2.5 2.8 3.2 | φ210 |
| 46–50×5 | 30 46 55 | 277.5 250 230 | 2950 | 41.98 49.71 53.80 | 55 | Y250M―2 | 54 63 64 | 2.5 2.8 3.2 | φ210 |
| 46–50×6 | 30 46 55 | 333 300 276 | 2950 | 50.38 59.65 64.56 | 75 | Y280S―2 | 54 63 64 | 2.5 2.8 3.2 | φ210 |
| 46–50×7 | 30 46 55 | 388.5 350 322 | 2950 | 58.78 69.60 75.32 | 90 | Y280M―2 | 54 63 64 | 2.5 2.8 3.2 | φ210 |
| 46–50×8 | 30 46 55 | 444 400 368 | 2950 | 67.20 79.52 86.08 | 90 | Y280M―2 | 54 63 64 | 2.5 2.8 3.2 | φ210 |
| 46–50×9 | 30 46 55 | 499.5 450 414 | 2950 | 75.56 89.48 96.84 | 110 | Y315S―2 | 54 63 64 | 2.5 2.8 3.2 | φ210 |
| 46–50×10 | 30 46 55 | 555 500 460 | 2950 | 83.97 99.42 107.60 | 132 | Y315M―2 | 54 63 64 | 2.5 2.8 3.2 | φ210 |
| 46–50×11 | 30 46 55 | 610.5 550 506 | 2950 | 92.37 109.36 118.36 | 132 | Y315M―2 | 54 63 64 | 2.5 2.8 3.2 | φ210 |
| 46–50×12 | 30 46 55 | 666 600 552 | 2950 | 100.8 119.28 129.12 | 132 | Y315M―2 | 54 63 64 | 2.5 2.8 3.2 | φ210 |
| 85–45×2 | 55 85 100 | 102 90 78 | 2950 | 24.25 28.92 30.35 | 37 | Y200L2―2 | 63 72 70 | 3.2 4.2 5.2 | φ200 |
| 85–45×3 | 55 85 100 | 153 135 117 | 2950 | 36.38 43.37 45.52 | 55 | Y250M―2 | 63 72 70 | 3.2 4.2 5.2 | φ200 |
| 85–45×4 | 55 85 100 | 204 180 156 | 2950 | 48.5 57.82 60.7 | 75 | Y280S―2 | 63 72 70 | 3.2 4.2 5.2 | φ200 |
| 85–45×5 | 55 85 100 | 255 225 195 | 2950 | 60.63 72.28 75.86 | 90 | Y280M―2 | 63 72 70 | 3.2 4.2 5.2 | φ200 |
| 85–45×6 | 55 85 100 | 306 270 234 | 2950 | 72.75 86.73 91.04 | 110 | Y315S―2 | 63 72 70 | 3.2 4.2 5.2 | φ200 |
| 85–45×7 | 55 85 100 | 357 315 273 | 2950 | 84.88 101.2 106.2 | 132 | Y315M―2 | 63 72 70 | 3.2 4.2 5.2 | φ200 |
| 85–45×8 | 55 85 100 | 408 360 312 | 2950 | 97.0 115.6 121.4 | 132 | Y315M―2 | 63 72 70 | 3.2 4.2 5.2 | φ200 |
| 85–45×9 | 55 85 100 | 459 405 351 | 2950 | 109.1 130.1 136.6 | 160 | Y315L1—2 | 63 72 70 | 3.2 4.2 5.2 | φ200 |
| 85-67×3 | 55 85 100 | 222 201 183 | 2950 | 57.3 68.4 73.3 | 90 | Y280M—2 | 58 68 68 | 3.3 4.0 4.4 | φ235 |
| 85-67×4 | 55 85 100 | 296 268 244 | 2950 | 76.4 91.2 97.7 | 110 | Y315S—2 | 58 68 68 | 3.3 4.0 4.4 | φ235 |
| 85-67×5 | 55 85 100 | 370 335 305 | 2950 | 95.6 114 122.2 | 132 | Y315M—2 | 58 68 68 | 3.3 4.0 4.4 | φ235 |
| 85-67×6 | 55 85 100 | 444 402 366 | 2950 | 114.7 136.9 146.6 | 160 | Y315L1—2 | 58 68 68 | 3.3 4.0 4.4 | φ235 |
| 85-67×7 | 55 85 100 | 518 469 427 | 2950 | 133.8 159.6 171 | 185 | Y315M1—2 | 58 68 68 | 3.3 4.0 4.4 | φ235 |
| 85-67×8 | 55 85 100 | 592 536 488 | 2950 | 152.9 182.4 195.4 | 220 | Y355M1—2 | 58 68 68 | 3.3 4.0 4.4 | φ235 |
| 85-67×9 | 55 85 100 | 666 603 549 | 2950 | 172 205.2 219.9 | 250 | Y355M2—2 | 58 68 68 | 3.3 4.0 4.4 | φ235 |
| 120-50×2 | 96 120 140 | 110 100 84.6 | 2950 | 39.44 44.54 48.8 | 55 | Y250M―2 | 73 73.3 67.5 | 3.2 5.1 6.7 | φ213 |
| 120-50×3 | 96 120 140 | 165 150 126.9 | 2950 | 59.09 66.88 71.68 | 90 | Y280M―2 | 73 73.3 67.5 | 3.2 5.1 6.7 | φ213 |
| 120-50×4 | 96 120 140 | 220 200 169.2 | 2950 | 78.79 89.17 95.57 | 110 | Y315S—2 | 73 73.3 67.5 | 3.2 5.1 6.7 | φ213 |
| 120-50×5 | 96 120 140 | 275 250 211.5 | 2950 | 98.49 111.46 119.46 | 132 | Y315M—2 | 73 73.3 67.5 | 3.2 5.1 6.7 | φ213 |
| 120-50×6 | 96 120 140 | 330 300 253.8 | 2950 | 118.18 133.75 143.36 | 160 | Y315L1—2 | 73 73.3 67.5 | 3.2 5.1 6.7 | φ213 |
| 120-50×7 | 96 120 140 | 385 350 296.1 | 2950 | 137.88 156.04 167.25 | 200 | Y315L2—2 | 73 73.3 67.5 | 3.2 5.1 6.7 | φ213 |
| 120-50×8 | 96 120 140 | 440 400 338.4 | 2950 | 157.58 178.33 191.14 | 200 | Y315L2—2 | 73 73.3 67.5 | 3.2 5.1 6.7 | φ213 |
| 120-50×9 | 96 120 140 | 495 450 380.7 | 2950 | 177.28 200.63 215.03 | 220 | Y355M1—2 | 73 73.3 67.5 | 3.2 5.1 6.7 | φ213 |
| 155-30×2 | 119 155 190 | 64 60 54 | 1480 | 29.8 33.71 36.95 | 45 | Y225M—4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |
| 155-30×3 | 119 155 190 | 96 90 81 | 1480 | 44.7 50.57 55.42 | 75 | Y280S—4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |
| 155-30×4 | 119 155 190 | 128 120 108 | 1480 | 59.6 67.42 73.9 | 90 | Y280M—4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |
| 155-30×5 | 119 155 190 | 160 150 135 | 1480 | 74.5 84.28 92.37 | 110 | Y315S—4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |
| 155-30×6 | 119 155 190 | 192 180 162 | 1480 | 89.4 101.1 110.8 | 132 | Y315M—4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |
| 155-30×7 | 119 155 190 | 224 210 189 | 1480 | 104.3 118.0 129.3 | 160 | Y315L1—4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |
| 155-30×8 | 119 155 190 | 256 240 216 | 1480 | 119.2 134.8 147.8 | 200 | Y315L2—4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |
| 155-30×9 | 119 155 190 | 288 270 243 | 1480 | 134.1 151.7 166.3 | 200 | Y315L2—4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |
| 155-30×10 | 119 155 190 | 320 300 270 | 1480 | 149 168.6 184.7 | 220 | Y355M1—4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |
| 155-67×2 | 100 155 185 | 152 134 118 | 2950 | 64.7 76.5 82.6 | 90 | Y280M—2 | 64 74 72 | 3.2 5.0 6.6 | φ235 |
| 155-67×3 | 100 155 185 | 228 201 177 | 2950 | 97.0 114.7 123.9 | 132 | Y315M—2 | 64 74 72 | 3.2 5.0 6.6 | φ235 |
| 155-67×4 | 100 155 185 | 304 268 236 | 2950 | 129.4 152.9 165.1 | 185 | Y315M1—2 | 64 74 72 | 3.2 5.0 6.6 | φ235 |
| 155-67×5 | 100 155 185 | 380 335 295 | 2950 | 161.7 191.2 206.4 | 220 | Y355M1—2 | 64 74 72 | 3.2 5.0 6.6 | φ235 |
| 155-67×6 | 100 155 185 | 456 402 354 | 2950 | 194 229.5 247.7 | 280 | Y355L1—2 | 64 74 72 | 3.2 5.0 6.6 | φ235 |
| 155-67×7 | 100 155 185 | 532 469 413 | 2950 | 226.4 267.7 288.9 | 315 | Y355L2—2 | 64 74 72 | 3.2 5.0 6.6 | φ235 |
| 155-67×8 | 100 155 185 | 608 536 472 | 2950 | 258.8 305.9 330.2 | 355 | Y3555—2 (6KV) | 64 74 72 | 3.2 5.0 6.6 | φ235 |
| 155-67×9 | 100 155 185 | 684 603 531 | 2950 | 291.1 344.2 371.5 | 400 | Y3556—2 (6KV) | 64 74 72 | 3.2 5.0 6.6 | φ235 |
| 280-43×2 | 185 280 335 | 94 86 76 | 1480 | 68.6 85.2 92.5 | 110 | Y315S—4 | 69 77 75 | 2.5 4.0 5.2 | φ360 |
| 280-43×3 | 185 280 335 | 141 129 114 | 1480 | 102.9 127.7 138.8 | 160 | Y315L1—4 | 69 77 75 | 2.5 4.0 5.2 | φ360 |
| 280-43×4 | 185 280 335 | 188 172 152 | 1480 | 137.7 170.3 185.0 | 200 | Y315L2—4 | 69 77 75 | 2.5 4.0 5.2 | φ360 |
| 280-43×5 | 185 280 335 | 235 215 190 | 1480 | 171.6 212.9 231.3 | 250 | Y355M2—4 | 69 77 75 | 2.5 4.0 5.2 | φ360 |
| 280-43×6 | 185 280 335 | 282 258 228 | 1480 | 205.9 255.5 277.5 | 315 | Y355L2—4 | 69 77 75 | 2.5 4.0 5.2 | φ360 |
| 280-43×7 | 185 280 335 | 329 301 266 | 1480 | 240.2 298.1 323.8 | 355 | Y4001—4 (6KV) | 69 77 75 | 2.5 4.0 5.2 | φ360 |
| 280-43×8 | 185 280 335 | 376 344 304 | 1480 | 274.5 340.7 370.0 | 400 | Y4002—4 (6KV) | 69 77 75 | 2.5 4.0 5.2 | φ360 |
| 280-43×9 | 185 280 335 | 423 387 342 | 1480 | 308.8 383.3 416.3 | 450 | Y4003—4 (6KV) | 69 77 75 | 2.5 4.0 5.2 | φ360 |
| 280-65×3 | 185 280 335 | 204 195 186 | 1480 | 180 215 239 | 280 | Y355L1—4 | 57 69 71 | 2.8 3.7 5.0 | φ430 |
| 280-65×4 | 185 280 335 | 272 260 248 | 1480 | 240 287 319 | 355 | Y4001—4 (6KV) | 57 69 71 | 2.8 3.7 5.0 | φ430 |
| 280-65×5 | 185 280 335 | 340 325 310 | 1480 | 300 359 398 | 450 | Y4003—4 (6KV) | 57 69 71 | 2.8 3.7 5.0 | φ430 |
| 280-65×6 | 185 280 335 | 408 390 372 | 1480 | 361 431 478 | 500 | Y4004—4 (6KV) | 57 69 71 | 2.8 3.7 5.0 | φ430 |
| 280-65×7 | 185 280 335 | 476 455 434 | 1480 | 421 503 558 | 630 | Y4501—4 (6KV) | 57 69 71 | 2.8 3.7 5.0 | φ430 |
| 280-65×8 | 185 280 335 | 544 520 496 | 1480 | 481 575 637 | 710 | Y4502—4 (6KV) | 57 69 71 | 2.8 3.7 5.0 | φ430 |
| 280-65×9 | 185 280 335 | 612 585 558 | 1480 | 541 646 717 | 800 | Y4503—4 (6KV) | 57 69 71 | 2.8 3.7 5.0 | φ430 |
| 280-65×10 | 185 280 335 | 680 650 620 | 1480 | 601 718 797 | 900 | Y4504—4 (6KV) | 57 69 71 | 2.8 3.7 5.0 | φ430 |
| 280-80×6 | 185 280 335 | 528 480 444 | 1480 | 451 523 570 | 630 | Y450—4 (6KV) | 59 70 71 | 2.8 3.5 5.0 | φ475 |
| 280-80×7 | 185 280 335 | 616 560 518 | 1480 | 526 610 665 | 800 | Y450—4 (6KV) | 59 70 71 | 2.8 3.5 5.0 | φ475 |
| 280-80×8 | 185 280 335 | 704 640 592 | 1480 | 601 697 760 | 900 | Y450—4 (6KV) | 59 70 71 | 2.8 3.5 5.0 | φ475 |
| 280-80×9 | 185 280 335 | 792 720 666 | 1480 | 677 785 855 | 1000 | Y500—4 (6KV) | 59 70 71 | 2.8 3.5 5.0 | φ475 |
| 280-80×10 | 185 280 335 | 880 800 740 | 1480 | 752 872 950 | 1120 | Y500—4 (6KV) | 59 70 71 | 2.8 3.5 5.0 | φ475 |
| 280-80×11 | 185 280 335 | 968 880 814 | 1480 | 827 959 1045 | 1120 | Y500—4 (6KV) | 59 70 71 | 2.8 3.5 5.0 | φ475 |
| 280-80×12 | 185 280 335 | 1056 960 888 | 1480 | 901 1046 1140 | 1250 | Y500—4 (6KV) | 59 70 71 | 2.8 3.5 5.0 | φ475 |
| 280-100×4 | 185 280 335 | 440 400 360 | 2980 | 369 396 421 | 500 | Y400—2 (6KV) | 60 77 78 | 5.0 5.6 6.2 | φ286 |
| 280-100×5 | 185 280 335 | 550 500 450 | 2980 | 461 495 526 | 630 | Y450—2 (6KV) | 60 77 78 | 5.0 5.6 6.2 | φ286 |
| 280-100×6 | 185 280 335 | 660 600 540 | 2980 | 553 594 631 | 800 | Y450—2 (6KV) | 60 77 78 | 5.0 5.6 6.2 | φ286 |
| 280-100×7 | 185 280 335 | 770 700 630 | 2980 | 645 693 736 | 900 | Y450—2 (6KV) | 60 77 78 | 5.0 5.6 6.2 | φ286 |
| 280-100×8 | 185 280 335 | 880 800 720 | 2980 | 739 792 842 | 1000 | Y450—2 (6KV) | 60 77 78 | 5.0 5.6 6.2 | φ286 |
| 280-100×9 | 185 280 335 | 990 900 810 | 2980 | 831 891 947 | 1120 | Y500—2 (6KV) | 60 77 78 | 5.0 5.6 6.2 | φ286 |
| 280-100×10 | 185 280 335 | 1100 1000 900 | 2980 | 923 990 1052 | 1250 | Y500—2 (6KV) | 60 77 78 | 5.0 5.6 6.2 | φ286 |
| 360-40×2 | 300 360 440 | 84 80 71 | 1480 | 89.1 98.1 110.5 | 132 | Y315M1—4 | 77 80 77 | 4.65 4.7 5.4 | φ360 |
| 360-40×3 | 300 360 440 | 126 120 106.5 | 1480 | 133.7 147.2 165.8 | 200 | Y315L2—4 | 77 80 77 | 4.65 4.7 5.4 | φ360 |
| 360-40×4 | 300 360 440 | 168 160 142 | 1480 | 178.3 196.2 221.1 | 250 | Y355M2—4 | 77 80 77 | 4.65 4.7 5.4 | φ360 |
| 360-40×5 | 300 360 440 | 210 200 177.5 | 1480 | 223.5 245.3 276.3 | 315 | Y355L2—4 | 77 80 77 | 4.65 4.7 5.4 | φ360 |
| 360-40×6 | 300 360 440 | 252 240 213 | 1480 | 257.4 294.1 331.5 | 400 | Y4002-4 (6KV) | 77 80 77 | 4.65 4.7 5.4 | φ360 |
| 360-40×7 | 300 360 440 | 294 280 248.5 | 1480 | 311.9 343.1 386.7 | 450 | Y4003-4 (6KV) | 77 80 77 | 4.65 4.7 5.4 | φ360 |
| 360-40×8 | 300 360 440 | 336 320 284 | 1480 | 356.5 392.2 441.9 | 500 | Y4004-4 (6KV) | 77 80 77 | 4.65 4.7 5.4 | φ360 |
| 360-40×9 | 300 360 440 | 378 360 319.5 | 1480 | 401.1 441.2 497.2 | 560 | Y4005-4 (6KV) | 77 80 77 | 4.65 4.7 5.4 | φ360 |
| 360-40×10 | 300 360 440 | 420 400 355 | 1480 | 445.6 490.2 552.4 | 630 | Y4501-4 (6KV) | 77 80 77 | 4.65 4.7 5.4 | φ360 |
| 450-60×2 | 335 450 500 | 130 120 113 | 1480 | 164.7 186.1 197.3 | 250 | Y355M2—4 | 72 79 78 | 4.1 5.2 6.3 | φ430 |
| 450-60×3 | 335 450 500 | 195 180 171 | 1480 | 247.1 279.2 296.0 | 355 | Y4001—4 | 72 79 78 | 4.1 5.2 6.3 | φ430 |
| 450-60×4 | 335 450 500 | 260 240 228 | 1480 | 329.5 372.2 394.7 | 500 | Y4004—4 (6KV) | 72 79 78 | 4.1 5.2 6.3 | φ430 |
| 450-60×5 | 335 450 500 | 325 300 285 | 1480 | 411.8 465.4 493.4 | 630 | Y4501—4 (6KV) | 72 79 78 | 4.1 5.2 6.3 | φ430 |
| 450-60×6 | 335 450 500 | 390 360 342 | 1480 | 494.2 558.3 592.0 | 710 | Y4502—4 (6KV) | 72 79 78 | 4.1 5.2 6.3 | φ430 |
| 450-60×7 | 335 450 500 | 455 420 399 | 1480 | 576.5 651.5 690.7 | 800 | Y4503—4 (6KV) | 72 79 78 | 4.1 5.2 6.3 | φ430 |
| 450-60×8 | 335 450 500 | 520 480 456 | 1480 | 658.9 744.4 789.4 | 900 | Y4504—4 (6KV) | 72 79 78 | 4.1 5.2 6.3 | φ430 |
| 450-60×9 | 335 450 500 | 585 540 513 | 1480 | 741.2 837.5 888.0 | 1000 | Y5001—4 (6KV) | 72 79 78 | 4.1 5.2 6.3 | φ430 |
| 450-60×10 | 335 450 500 | 650 600 570 | 1480 | 823.6 930.8 995.1 | 1120 | Y5002—4 (6KV) | 72 79 78 | 4.1 5.2 6.3 | φ430 |
| 450-90×2 | 335 450 500 | 188 180 172 | 1480 | 252.1 282.7 296.3 | 355 | YB450S2—4 (6KV) | 68 78 79 | 3.6 4 4.6 | φ510 |
| 450-90×3 | 335 450 500 | 282 270 258 | 1480 | 378.1 424 444.5 | 500 | YB560S1—4 (6KV) | 68 78 79 | 3.6 4 4.6 | φ510 |
| 450-90×4 | 335 450 500 | 376 360 344 | 1480 | 504.2 565.3 592.7 | 710 | YB560M1-4 (6KV) | 68 78 79 | 3.6 4 4.6 | φ510 |
| 450-90×5 | 335 450 500 | 470 450 430 | 1480 | 630.3 706.6 740.9 | 800 | YB630S1—4 (6KV) | 68 78 79 | 3.6 4 4.6 | φ510 |
| 450-90×6 | 335 450 500 | 564 540 516 | 1480 | 756.4 847.9 889.1 | 1000 | YB630M1-4 (6KV) | 68 78 79 | 3.6 4 4.6 | φ510 |
| 450-90×7 | 335 450 500 | 658 630 602 | 1480 | 882.5 989.2 1037.3 | 1120 | YB630M2-4 (6KV) | 68 78 79 | 3.6 4 4.6 | φ510 |
| 450-90×8 | 335 450 500 | 752 720 688 | 1480 | 1008.4 1130.6 1185.4 | 1250 | YB710S1—4 (6KV) | 68 78 79 | 3.6 4 4.6 | φ510 |
| 450-90×9 | 335 450 500 | 846 810 774 | 1480 | 1134.6 1271.9 1333.7 | 1400 | YB710S2-4 (6KV) | 68 78 79 | 3.6 4 4.6 | φ510 |
| 450-90×10 | 335 450 500 | 940 900 860 | 1480 | 1260.6 1413.2 1481.8 | 1600 | YB710M1-4 (6KV) | 68 78 79 | 3.6 4 4.6 | φ510 |
| 450-90×11 | 335 450 500 | 1034 990 946 | 1480 | 1386.7 1554.5 1630 | 1800 | YB710M2-4 (6KV) | 68 78 79 | 3.6 4 4.6 | φ510 |
| 450-90×12 | 335 450 500 | 1128 1080 1032 | 1480 | 1512.7 1695.8 1778.2 | 2000 | YB800S1-4 (6KV) | 68 78 79 | 3.6 4 4.6 | φ510 |
| 550-50×2 | 450 550 590 | 120 100 90 | 1480 | 188.5 189.6 192.7 | 250 | Y3554—4 | 78 79 75 | 5.2 5.8 6.5 | φ430 |
| 550-50×3 | 450 550 590 | 180 150 135 | 1480 | 282.8 284.3 289.1 | 355 | Y4001—4 (6KV) | 78 79 75 | 5.2 5.8 6.5 | φ430 |
| 550-50×4 | 450 550 590 | 240 200 180 | 1480 | 376.9 378.9 385.4 | 450 | Y4003—4 (6KV) | 78 79 75 | 5.2 5.8 6.5 | φ430 |
| 550-50×5 | 450 550 590 | 300 250 225 | 1480 | 471.3 473.8 481.8 | 560 | Y4005—4 (6KV) | 78 79 75 | 5.2 5.8 6.5 | φ430 |
| 550-50×6 | 450 550 590 | 360 300 270 | 1480 | 565.5 568.5 578.1 | 710 | Y4502—4 (6KV) | 78 79 75 | 5.2 5.8 6.5 | φ430 |
| 550-50×7 | 450 550 590 | 420 350 315 | 1480 | 659.8 663.3 674.5 | 800 | Y4503—4 (6KV) | 78 79 75 | 5.2 5.8 6.5 | φ430 |
| 550-50×8 | 450 550 590 | 480 400 360 | 1480 | 754.0 758.0 770.8 | 900 | Y4504—4 (6KV) | 78 79 75 | 5.2 5.8 6.5 | φ430 |
| 550-50×9 | 450 550 590 | 540 450 405 | 1480 | 848.3 852.8 867.2 | 1000 | Y5003—4 (6KV) | 78 79 75 | 5.2 5.8 6.5 | φ430 |
| 650-70×2 | 550 650 750 | 147 140 120 | 1480 | 293.5 323.8 326.7 | 400 | Y4002—4 (6KV) | 75 76.5 75 | 5.8 6.2 6.5 | φ493 |
| 650-70×3 | 550 650 750 | 220.5 210 180 | 1480 | 440.2 485.7 490.0 | 560 | Y4005-4 (6KV) | 75 76.5 75 | 5.8 6.2 6.5 | φ493 |
| 650-70×4 | 550 650 750 | 294 280 240 | 1480 | 586.9 647.6 653.3 | 710 | Y4502—4 (6KV) | 75 76.5 75 | 5.8 6.2 6.5 | φ493 |
| 650-70×5 | 550 650 750 | 367.5 350 300 | 1480 | 733.6 809.5 816.7 | 900 | Y4504—4 (6KV) | 75 76.5 75 | 5.8 6.2 6.5 | φ493 |
| 650-70×6 | 550 650 750 | 441 420 360 | 1480 | 880.4 971.5 980.0 | 1120 | Y5002—4 (6KV) | 75 76.5 75 | 5.8 6.2 6.5 | φ493 |
| 650-70×7 | 550 650 750 | 514.5 490 420 | 1480 | 1027.1 1133.4 1143.3 | 1250 | Y5003—4 (6KV) | 75 76.5 75 | 5.8 6.2 6.5 | φ493 |
| 650-70×8 | 550 650 750 | 588 560 480 | 1480 | 1173.8 1295.3 1306.7 | 1600 | Y5603—4 (10KV) | 75 76.5 75 | 5.8 6.2 6.5 | φ493 |
| 740-80×2 | 640 740 840 | 168.4 160 146.6 | 1480 | 378.5 411.2 433.6 | 500 | Y4004—4 (6KV) | 77.5 78.4 77.3 | 5.8 6.2 6.5 | φ493 |
| 740-80×3 | 640 740 840 | 252.6 240 219.9 | 1480 | 567.9 616.8 650.4 | 710 | Y4502—4 (6KV) | 77.5 78.4 77.3 | 5.8 6.2 6.5 | φ493 |
| 740-80×4 | 640 740 840 | 336.8 320 293.2 | 1480 | 757.2 822.4 867.2 | 1000 | Y5001—4 (6KV) | 77.5 78.4 77.3 | 5.8 6.2 6.5 | φ493 |
| 740-80×5 | 640 740 840 | 421 400 366.5 | 1480 | 946.5 1028 1084 | 1250 | Y5003—4 (6KV) | 77.5 78.4 77.3 | 5.8 6.2 6.5 | φ493 |
| 740-80×6 | 640 740 840 | 505.2 480 439.8 | 1480 | 1135.8 1233.6 1300.8 | 1600 | Y5603—4 (10KV) | 77.5 78.4 77.3 | 5.8 6.2 6.5 | φ493 |
| 80D12×2 | 21.6 34.6 39.6 | 28.8 22.8 19.0 | 2950 | 2.46 2.84 2.82 | 4 | Y112M—2 | 69 75 72 | 3.2 3.3 3.4 | φ110 |
| 80D12×3 | 21.6 34.6 39.6 | 43.2 34.2 28.5 | 2950 | 3.69 4.26 4.23 | 5.5 | Y132S1—2 | 69 75 72 | 3.2 3.3 3.4 | φ110 |
| 80D12×4 | 21.6 34.6 39.6 | 57.6 45.6 38.0 | 2950 | 4.92 5.69 5.64 | 7.5 | Y132S2—2 | 69 75 72 | 3.2 3.3 3.4 | φ110 |
| 80D12×5 | 21.6 34.6 39.6 | 72.0 57.0 47.5 | 2950 | 6.15 7.10 7.05 | 11 | Y160M1—2 | 69 75 72 | 3.2 3.3 3.4 | φ110 |
| 80D12×6 | 21.6 34.6 39.6 | 86.4 68.4 57.0 | 2950 | 7.38 8.52 8.46 | 11 | Y160M1—2 | 69 75 72 | 3.2 3.3 3.4 | φ110 |
| 80D12×7 | 21.6 34.6 39.6 | 100.8 79.8 66.5 | 2950 | 8.61 9.94 9.87 | 15 | Y160M2—2 | 69 75 72 | 3.2 3.3 3.4 | φ110 |
| 80D12×8 | 21.6 34.6 39.6 | 115.2 91.2 76.0 | 2950 | 9.84 11.36 11.28 | 15 | Y160M2—2 | 69 75 72 | 3.2 3.3 3.4 | φ110 |
| 80D12×9 | 21.6 34.6 39.6 | 129.6 102.6 85.5 | 2950 | 11.07 12.78 12.69 | 18.5 | Y160L—2 | 69 75 72 | 3.2 3.3 3.4 | φ110 |
| 80D30×3 | 26 43 48 | 102 90 83 | 2950 | 12.0 15.1 15.7 | 18.5 | Y160L—2 | 60 70 69 | 3.0 3.9 4.3 | φ162 |
| 80D30×4 | 26 43 48 | 136 120 111 | 2950 | 16.0 20.1 21.0 | 22 | Y180M—2 | 60 70 69 | 3.0 3.9 4.3 | φ162 |
| 80D30×5 | 26 43 48 | 170 150 139 | 2950 | 20.1 25.2 26.2 | 30 | Y200L1—2 | 60 70 69 | 3.0 3.9 4.3 | φ162 |
| 80D30×6 | 26 43 48 | 204 180 167 | 2950 | 24.1 30.2 31.4 | 37 | Y200L2—2 | 60 70 69 | 3.0 3.9 4.3 | φ162 |
| 80D30×7 | 26 43 48 | 238 210 195 | 2950 | 28.1 35.2 36.7 | 45 | Y225M—2 | 60 70 69 | 3.0 3.9 4.3 | φ162 |
| 80D30×8 | 26 43 48 | 272 240 222 | 2950 | 32.1 40.2 42.0 | 55 | Y250M—2 | 60 70 69 | 3.0 3.9 4.3 | φ162 |
| 80D30×9 | 26 43 48 | 306 270 250 | 2950 | 36.1 45.3 47.2 | 55 | Y250M—2 | 60 70 69 | 3.0 3.9 4.3 | φ162 |
| 80D30×10 | 26 43 48 | 340 300 278 | 2950 | 40.1 50.3 53.0 | 55 | Y250M—2 | 60 70 69 | 3.0 3.9 4.3 | φ162 |
| 100D16×2 | 36 54 72 | 40 32 22 | 2950 | 5.94 6.44 6.53 | 7.5 | Y132S2—2 | 66 73 66 | 3.7 3.9 4.3 | φ128 |
| 100D16×3 | 36 54 72 | 60 48 34 | 2950 | 8.91 9.67 9.80 | 15 | Y160M2—4 | 66 73 66 | 3.7 3.9 4.3 | φ128 |
| 100D16×4 | 36 54 72 | 80 64 45 | 2950 | 11.88 12.89 13.07 | 18.5 | Y160 L—2 | 66 73 66 | 3.7 3.9 4.3 | φ128 |
| 100D16×5 | 36 54 72 | 100 80 56 | 2950 | 14.85 16.11 16.33 | 22 | Y180M—2 | 66 73 66 | 3.7 3.9 4.3 | φ128 |
| 100D16×6 | 36 54 72 | 120 96 67 | 2950 | 17.82 19.33 19.60 | 22 | Y180M—2 | 66 73 66 | 3.7 3.9 4.3 | φ128 |
| 100D16×7 | 36 54 72 | 140 112 78 | 2950 | 20.79 22.55 22.87 | 30 | Y200L1-2 | 66 73 66 | 3.7 3.9 4.3 | φ128 |
| 100D16×8 | 36 54 72 | 160 128 90 | 2950 | 23.76 25.78 26.13 | 30 | Y200L1-2 | 66 73 66 | 3.7 3.9 4.3 | φ128 |
| 100D16×9 | 36 54 72 | 180 144 101 | 2950 | 26.73 29.00 29.40 | 37 | Y200L2-2 | 66 73 66 | 3.7 3.9 4.3 | φ128 |
| 100D45×2 | 55 85 100 | 102 90 78 | 2950 | 24.25 28.92 30.35 | 37 | Y200L2-2 | 63 72 70 | 3.2 4.2 5.2 | φ200 |
| 100D45×3 | 55 85 100 | 153 135 117 | 2950 | 36.38 43.37 45.52 | 55 | Y250M-2 | 63 72 70 | 3.2 4.2 5.2 | φ200 |
| 100D45×4 | 55 85 100 | 204 180 156 | 2950 | 48.50 57.82 60.70 | 75 | Y280S-2 | 63 72 70 | 3.2 4.2 5.2 | φ200 |
| 100D45×5 | 55 85 100 | 255 225 195 | 2950 | 60.63 72.28 75.86 | 90 | Y280M-2 | 63 72 70 | 3.2 4.2 5.2 | φ200 |
| 100D45×6 | 55 85 100 | 306 270 234 | 2950 | 72.75 86.73 91.04 | 110 | Y315S-2 | 63 72 70 | 3.2 4.2 5.2 | φ200 |
| 100D45×7 | 55 85 100 | 357 315 273 | 2950 | 84.88 101.2 106.2 | 132 | Y315M-2 | 63 72 70 | 3.2 4.2 5.2 | φ200 |
| 100D45×8 | 55 85 100 | 408 360 312 | 2950 | 97.0 115.6 121.4 | 132 | Y315M-2 | 63 72 70 | 3.2 4.2 5.2 | φ200 |
| 100D45×9 | 55 85 100 | 459 405 351 | 2950 | 109.1 130.1 136.6 | 160 | Y315L1-2 | 63 72 70 | 3.2 4.2 5.2 | φ200 |
| 125D25×2 | 72 101 119 | 51.2 43.0 35.0 | 2950 | 14.20 15.20 15.30 | 22 | Y180M-2 | 70.5 77.5 77.0 | 3.2 3.6 4.3 | φ156 |
| 125D25×3 | 72 101 119 | 76.8 64.5 52.5 | 2950 | 21.30 22.80 22.90 | 30 | Y200L1-2 | 70.5 77.5 77.0 | 3.2 3.6 4.3 | φ156 |
| 125D25×4 | 72 101 119 | 102.4 86.0 70.0 | 2950 | 28.40 30.40 30.60 | 37 | Y200L2-2 | 70.5 77.5 77.0 | 3.2 3.6 4.3 | φ156 |
| 125D25×5 | 72 101 119 | 128.0 107.5 87.5 | 2950 | 35.50 38.00 38.25 | 45 | Y225M-2 | 70.5 77.5 77.0 | 3.2 3.6 4.3 | φ156 |
| 125D25×6 | 72 101 119 | 153.6 129.0 105.0 | 2950 | 42.60 45.60 45.90 | 55 | Y250M-2 | 70.5 77.5 77.0 | 3.2 3.6 4.3 | φ156 |
| 125D25×7 | 72 101 119 | 179.2 150.5 122.5 | 2950 | 49.70 53.20 53.55 | 75 | Y280S-2 | 70.5 77.5 77.0 | 3.2 3.6 4.3 | φ156 |
| 125D25×8 | 72 101 119 | 204.8 172.0 140.0 | 2950 | 56.80 60.80 61.20 | 75 | Y280S-2 | 70.5 77.5 77.0 | 3.2 3.6 4.3 | φ156 |
| 125D25×9 | 72 101 119 | 230.4 193.5 157.5 | 2950 | 63.90 68.40 68.85 | 90 | Y280M-2 | 70.5 77.5 77.0 | 3.2 3.6 4.3 | φ156 |
| 150D30×2 | 119 155 190 | 64 60 54 | 1480 | 29.80 33.71 36.95 | 45 | Y225M-4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |
| 150D30×3 | 119 155 190 | 96 90 81 | 1480 | 44.70 50.57 55.42 | 75 | Y280S-4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |
| 150D30×4 | 119 155 190 | 128 120 108 | 1480 | 59.60 67.42 73.90 | 90 | Y280M-4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |
| 150D30×5 | 119 155 190 | 160 150 135 | 1480 | 74.50 84.28 92.37 | 110 | Y315S-4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |
| 150D30×6 | 119 155 190 | 192 180 162 | 1480 | 89.4 101.1 110.8 | 132 | Y315M-4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |
| 150D30×7 | 119 155 190 | 224 210 189 | 1480 | 104.3 118.0 129.3 | 160 | Y315L1-4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |
| 150D30×8 | 119 155 190 | 256 240 216 | 1480 | 119.2 134.8 147.8 | 200 | Y315L2-4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |
| 150D30×9 | 119 155 190 | 288 270 243 | 1480 | 134.1 151.7 166.3 | 200 | Y315L2-4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |
| 150D30×10 | 119 155 190 | 320 300 270 | 1480 | 149.0 168.6 184.7 | 220 | Y315M1-4 | 69.5 75 76 | 3.2 3.9 4.8 | φ305 |

注：上表中的型号△-◇×□适用于D、DM、DF、DY；△D◇×□也适用于D、DM、DF、DY。

Note: the type in the sheet such as △-◇×□ and △D◇×□ are applied to D、DM、DF、DY.

外形安装尺寸图（共用底座）

Overall installing dimension Drawing（with Common Base）

外形安装尺寸图（本身底座）

Overall installing dimension Drawing（without Common Base）

| D、DM、DF、DY6-25型泵外形安装尺寸表(公用底座) Overall installing dimension sheet(with common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 级数 | L | L1 | L2 | L3 | L4 | L5 | L6 | L7 | L8 | C | B1 | B2 | B3 | H | H1 | H2 | h | n-φd |
| 2 | 1047 | 855 | - | 575 | 145 | 240 | 130 | 275 | 85 | 2 | 350 | 350 | 170 | 275 | 170 | 100 | 30 | 4-φ24 |
| 3 | 1192 | 965 | - | 645 | 190 | 240 | 180 | 275 | 55 | 2 | 370 | 370 | 170 | 275 | 170 | 132 | 30 | 4-φ24 |
| 4 | 1242 | 965 | - | 645 | 190 | 240 | 230 | 275 | 105 | 2 | 370 | 370 | 170 | 275 | 170 | 132 | 30 | 4-φ24 |
| 5 | 1292 | 965 | - | 645 | 190 | 240 | 280 | 275 | 155 | 2 | 370 | 370 | 170 | 275 | 170 | 132 | 30 | 4-φ24 |
| 6 | 1478 | 1215 | - | 820 | 230 | 240 | 330 | 275 | 105 | 2 | 360 | 430 | 170 | 260 | 170 | 160 | 30 | 4-φ24 |
| 7 | 1528 | 1215 | - | 820 | 230 | 240 | 380 | 275 | 155 | 2 | 360 | 430 | 170 | 260 | 170 | 160 | 30 | 4-φ24 |
| 8 | 1578 | 1430 | - | 920 | 300 | 240 | 430 | 275 | 170 | 2 | 410 | 480 | 170 | 270 | 170 | 160 | 35 | 4-φ24 |
| 9 | 1628 | 1430 | - | 920 | 300 | 240 | 480 | 275 | 170 | 2 | 410 | 480 | 170 | 270 | 170 | 160 | 35 | 4-φ24 |
| 10 | 1723 | 1500 | - | 990 | 350 | 240 | 530 | 275 | 170 | 2 | 365 | 460 | 170 | 280 | 170 | 160 | 40 | 4-φ24 |
| 11 | 1773 | 1500 | - | 990 | 350 | 240 | 580 | 275 | 220 | 2 | 365 | 460 | 170 | 280 | 170 | 160 | 40 | 4-φ24 |
| 12 | 1823 | 1500 | - | 990 | 350 | 240 | 630 | 275 | 270 | 2 | 365 | 460 | 170 | 280 | 170 | 160 | 40 | 4-φ24 |
| D、DM、DF、DY 6-50型泵外形安装尺寸表(公用底座) Overall installing dimension sheet(with common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 级数 | L | L1 | L2 | L3 | L4 | L5 | L6 | L7 | L8 | C | B1 | B2 | B3 | H | H1 | H2 | h | n-φd |
| 2 | 1407 | 1170 | - | 840 | 190 | 284 | 160 | 343 | 5 | 2 | 480 | 480 | 215 | 260 | 215 | 160 | 35 | 4-φ24 |
| 3 | 1467 | 1170 | - | 840 | 190 | 284 | 220 | 343 | 70 | 2 | 480 | 480 | 215 | 260 | 215 | 160 | 35 | 4-φ24 |
| 4 | 1572 | 1230 | - | 845 | 210 | 284 | 280 | 343 | 140 | 2 | 460 | 460 | 215 | 260 | 215 | 160 | 35 | 4-φ24 |
| 5 | 1654 | 1310 | - | 880 | 240 | 284 | 340 | 343 | 190 | 2 | 465 | 465 | 215 | 260 | 215 | 180 | 35 | 4-φ24 |
| 6 | 1822 | 1650 | - | 990 | 415 | 284 | 400 | 343 | 155 | 2 | 445 | 510 | 215 | 280 | 215 | 200 | 35 | 4-φ24 |
| 7 | 1882 | 1650 | - | 990 | 415 | 284 | 460 | 343 | 215 | 2 | 445 | 510 | 215 | 280 | 215 | 200 | 35 | 4-φ24 |
| 8 | 1942 | 1650 | - | 990 | 415 | 284 | 520 | 343 | 275 | 2 | 445 | 510 | 215 | 280 | 215 | 200 | 35 | 4-φ24 |
| 9 | 2002 | 1650 | - | 990 | 415 | 284 | 580 | 343 | 335 | 2 | 445 | 510 | 215 | 280 | 215 | 200 | 35 | 4-φ24 |
| 10 | 2097 | 1750 | - | 1305 | 220 | 284 | 640 | 343 | 155 | 2 | 470 | 545 | 215 | 305 | 215 | 225 | 35 | 4-φ24 |
| 11 | 2157 | 1750 | - | 1305 | 220 | 284 | 700 | 343 | 215 | 2 | 470 | 545 | 215 | 305 | 215 | 225 | 35 | 4-φ24 |
| 12 | 2335 | 2000 | 600 | 1200 | 400 | 284 | 760 | 343 | 329 | 2 | 460 | 595 | 215 | 330 | 215 | 250 | 35 | 6-φ30 |
| D、DM、DF、DY 12-25型泵外形安装尺寸表(公用底座) Overall installing dimension sheet(with common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 级数 | L | L1 | L2 | L3 | L4 | L5 | L6 | L7 | L8 | C | B1 | B2 | B3 | H | H1 | H2 | h | n-φd |
| 2 | 1067 | 965 | - | 645 | 190 | 240 | 130 | 275 | -5 | 2 | 370 | 370 | 170 | 250 | 170 | 132 | 30 | 4-φ24 |
| 3 | 1192 | 965 | - | 645 | 190 | 240 | 180 | 275 | 55 | 2 | 370 | 370 | 170 | 250 | 170 | 132 | 30 | 4-φ24 |
| 4 | 1378 | 1120 | - | 745 | 205 | 240 | 230 | 275 | 75 | 2 | 360 | 440 | 170 | 255 | 170 | 160 | 35 | 4-φ24 |
| 5 | 1428 | 1120 | - | 745 | 205 | 240 | 280 | 275 | 125 | 2 | 360 | 440 | 170 | 255 | 170 | 160 | 35 | 4-φ24 |
| 6 | 1478 | 1215 | - | 820 | 230 | 240 | 330 | 275 | 105 | 2 | 360 | 430 | 170 | 255 | 170 | 160 | 30 | 4-φ24 |
| 7 | 1528 | 1215 | - | 820 | 230 | 240 | 380 | 275 | 155 | 2 | 360 | 430 | 170 | 255 | 170 | 160 | 30 | 4-φ24 |
| 8 | 1623 | 1430 | - | 920 | 300 | 240 | 430 | 275 | 170 | 2 | 410 | 480 | 170 | 270 | 170 | 160 | 35 | 4-φ24 |
| 9 | 1673 | 1430 | - | 920 | 300 | 240 | 480 | 275 | 170 | 2 | 410 | 480 | 170 | 270 | 170 | 160 | 35 | 4-φ24 |
| 10 | 1743 | 1490 | - | 975 | 355 | 240 | 530 | 275 | 185 | 2 | 365 | 470 | 170 | 280 | 170 | 180 | 30 | 4-φ24 |
| 11 | 1793 | 1490 | - | 975 | 355 | 240 | 580 | 275 | 235 | 2 | 365 | 470 | 170 | 280 | 170 | 180 | 30 | 4-φ24 |
| 12 | 1952 | 1640 | - | 965 | 445 | 240 | 630 | 275 | 365 | 2 | 350 | 500 | 170 | 350 | 170 | 200 | 45 | 4-φ24 |

| D、DM、DF、DY 12-50型泵外形安装尺寸表(共用底座) Overall installing dimension sheet(with common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 级数 |  | L | L1 |  | L2 | L3 | L4 | L5 | L6 | L7 | L8 | C | B1 | B2 | B3 | H | H1 | H2 | h | n-φd |
| 2 |  | 1412 | 1230 |  | - | 845 | 210 | 284 | 160 | 345 | 15 | 5 | 460 | 460 | 215 | 260 | 215 | 160 | 30 | 4-φ24 |
| 3 |  | 1517 | 1230 |  | - | 845 | 210 | 284 | 220 | 345 | 75 | 5 | 460 | 460 | 215 | 260 | 215 | 160 | 30 | 4-φ24 |
| 4 |  | 1597 | 1310 |  | - | 880 | 240 | 284 | 280 | 345 | 130 | 5 | 465 | 465 | 215 | 260 | 215 | 180 | 30 | 4-φ24 |
| 5 |  | 1762 | 1650 |  | - | 990 | 415 | 284 | 340 | 345 | 120 | 5 | 445 | 510 | 215 | 280 | 215 | 180 | 35 | 4-φ24 |
| 6 |  | 1822 | 1650 |  | - | 990 | 415 | 284 | 400 | 345 | 185 | 5 | 445 | 510 | 215 | 280 | 215 | 200 | 35 | 4-φ24 |
| 7 |  | 1882 | 1650 |  | - | 990 | 415 | 284 | 460 | 345 | 245 | 5 | 445 | 510 | 215 | 280 | 215 | 200 | 35 | 4-φ24 |
| 8 |  | 1982 | 1750 |  | - | 1305 | 220 | 284 | 520 | 345 | -5 | 5 | 470 | 545 | 215 | 315 | 215 | 225 | 35 | 4-φ24 |
| 9 |  | 2042 | 1750 |  | - | 1305 | 220 | 284 | 580 | 345 | 55 | 5 | 470 | 545 | 215 | 315 | 215 | 225 | 35 | 4-φ24 |
| 10 |  | 2204 | 1870 |  | 500 | 1200 | 420 | 284 | 640 | 345 | 288 | 5 | 460 | 595 | 215 | 330 | 215 | 250 | 35 | 6-φ30 |
| 11 |  | 2264 | 1870 |  | 500 | 1200 | 420 | 284 | 700 | 345 | 348 | 5 | 460 | 595 | 215 | 330 | 215 | 250 | 35 | 6-φ30 |
| 12 |  | 2407 | 2000 |  | 600 | 1300 | 400 | 284 | 760 | 345 | 329 | 5 | 460 | 645 | 215 | 360 | 215 | 280 | 35 | 6-φ30 |
| D、DM、DF、DY 25-30型泵外形安装尺寸表(共用底座) Overall installing dimension sheet(with common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 级数 |  | L | L1 | L2 |  | L3 | L4 | L5 | L6 | L7 | L8 | C | B1 | B2 | B3 | H | H1 | H2 | h | n-φd |
| 2 |  | 1416 | 1170 | - |  | 840 | 190 | 285 | 165 | 345 | 5 | 5 | 480 | 480 | 210 | 260 | 210 | 160 | 35 | 4-φ24 |
| 3 |  | 1481 | 1170 | - |  | 840 | 190 | 285 | 230 | 345 | 70 | 5 | 480 | 480 | 210 | 260 | 210 | 160 | 35 | 4-φ24 |
| 4 |  | 1591 | 1230 | - |  | 845 | 210 | 285 | 295 | 345 | 140 | 5 | 460 | 460 | 210 | 260 | 210 | 160 | 35 | 4-φ24 |
| 5 |  | 1680 | 1310 | - |  | 880 | 240 | 285 | 360 | 345 | 190 | 5 | 465 | 465 | 210 | 260 | 210 | 180 | 30 | 4-φ24 |
| 6 |  | 1850 | 1440 | - |  | 930 | 310 | 285 | 425 | 345 | 210 | 5 | 465 | 510 | 210 | 280 | 210 | 200 | 35 | 4-φ24 |
| 7 |  | 1915 | 1650 | - |  | 990 | 415 | 285 | 490 | 345 | 245 | 5 | 445 | 510 | 210 | 280 | 210 | 200 | 35 | 4-φ24 |
| 8 |  | 1980 | 1650 | - |  | 990 | 415 | 285 | 555 | 345 | 310 | 5 | 445 | 510 | 210 | 280 | 210 | 200 | 35 | 4-φ24 |
| 9 |  | 2045 | 1650 | - |  | 990 | 415 | 285 | 620 | 345 | 375 | 5 | 445 | 510 | 210 | 280 | 210 | 200 | 35 | 4-φ24 |
| 10 |  | 2150 | 1750 | - |  | 1305 | 220 | 285 | 685 | 345 | 155 | 5 | 470 | 545 | 210 | 315 | 210 | 225 | 35 | 4-φ24 |
| D、DM、DF、DY 25-50型泵外形安装尺寸表(共用底座) Overall installing dimension sheet(with common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 级数 | L |  | L1 | L2 |  | L3 | L4 | L5 | L6 | L7 | L8 | C | B1 | B2 | B3 | H | H1 | H2 | h | n-φd |
| 3 | 1637 |  | 1240 | - |  | 665 | 280 | 355 | 250 | 345 | 175 | 2 | 500 | 500 | 300 | 360 | 270 | 180 | 40 | 4-φ24 |
| 4 | 1802 |  | 1430 | - |  | 900 | 250 | 355 | 310 | 345 | 100 | 2 | 520 | 520 | 300 | 320 | 270 | 200 | 45 | 4-φ24 |
| 5 | 1862 |  | 1430 | - |  | 900 | 250 | 355 | 370 | 345 | 160 | 2 | 520 | 520 | 300 | 320 | 270 | 200 | 45 | 4-φ24 |
| 6 | 1962 |  | 1560 | 530 |  | 1060 | 235 | 355 | 430 | 345 | 165 | 2 | 560 | 560 | 300 | 365 | 270 | 225 | 40 | 6-φ30 |
| 7 | 2137 |  | 1740 | 555 |  | 1120 | 360 | 355 | 490 | 345 | 125 | 2 | 530 | 600 | 300 | 350 | 270 | 250 | 40 | 6-φ30 |
| 8 | 2267 |  | 2040 | 725 |  | 1470 | 380 | 355 | 550 | 345 | 120 | 2 | 500 | 720 | 300 | 430 | 270 | 280 | 40 | 6-φ30 |
| 9 | 2327 |  | 2040 | 725 |  | 1470 | 380 | 355 | 610 | 345 | 110 | 2 | 500 | 720 | 300 | 430 | 270 | 280 | 40 | 6-φ30 |
| 10 | 2387 |  | 2040 | 725 |  | 1470 | 380 | 355 | 670 | 345 | 170 | 2 | 500 | 720 | 300 | 430 | 270 | 280 | 40 | 6-φ30 |
| 11 | 2497 |  | 2040 | 725 |  | 1470 | 380 | 355 | 730 | 345 | 230 | 2 | 500 | 720 | 300 | 430 | 270 | 280 | 40 | 6-φ30 |
| 12 | 2753 |  | 2200 | 745 |  | 1490 | 370 | 355 | 790 | 345 | 270 | 2 | 510 | 730 | 300 | 440 | 270 | 315 | 50 | 6-φ30 |

| D、DM、DF、DY 46-30型泵外形安装尺寸表(共用底座) Overall installing dimension sheet(with common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 级数 |  |  |  | L |  |  |  |  | L1 |  |  |  |  | L2 |  |  |  |  |  | L3 |  |  |  | L4 |  |  |  |  |  |  | L5 |  |  |  | L6 |  |  | L7 |  |  |  | L8 |  |  |  |  | C |  |  | B1 |  |  |  | B2 |  |  |  |  | B3 |  |  |  | H |  |  |  |  | H1 |  |  |  | H2 |  |  |  | h | n-φd |  |  |  |
| 2 |  |  |  | 1416 |  |  |  |  | 1170 |  |  |  |  | - |  |  |  |  |  | 840 |  |  |  | 190 |  |  |  |  |  |  | 280 |  |  |  | 165 |  |  | 345 |  |  |  | 5 |  |  |  |  | 5 |  |  | 485 |  |  |  | 485 |  |  |  |  | 210 |  |  |  | 260 |  |  |  |  | 210 |  |  |  | 160 |  |  |  | 40 | 4-φ24 |  |  |  |
| 3 |  |  |  | 1546 |  |  |  |  | 1170 |  |  |  |  | - |  |  |  |  |  | 840 |  |  |  | 140 |  |  |  |  |  |  | 280 |  |  |  | 230 |  |  | 345 |  |  |  | 130 |  |  |  |  | 5 |  |  | 485 |  |  |  | 485 |  |  |  |  | 210 |  |  |  | 260 |  |  |  |  | 210 |  |  |  | 180 |  |  |  | 40 | 4-φ24 |  |  |  |
| 4 |  |  |  | 1720 |  |  |  |  | 1440 |  |  |  |  | - |  |  |  |  |  | 930 |  |  |  | 310 |  |  |  |  |  |  | 280 |  |  |  | 295 |  |  | 345 |  |  |  | 140 |  |  |  |  | 5 |  |  | 465 |  |  |  | 510 |  |  |  |  | 210 |  |  |  | 280 |  |  |  |  | 210 |  |  |  | 200 |  |  |  | 30 | 4-φ24 |  |  |  |
| 5 |  |  |  | 1785 |  |  |  |  | 1440 |  |  |  |  | - |  |  |  |  |  | 930 |  |  |  | 310 |  |  |  |  |  |  | 280 |  |  |  | 360 |  |  | 345 |  |  |  | 190 |  |  |  |  | 5 |  |  | 465 |  |  |  | 510 |  |  |  |  | 210 |  |  |  | 280 |  |  |  |  | 210 |  |  |  | 200 |  |  |  | 30 | 4-φ24 |  |  |  |
| 6 |  |  |  | 1855 |  |  |  |  | 1440 |  |  |  |  | - |  |  |  |  |  | 930 |  |  |  | 310 |  |  |  |  |  |  | 280 |  |  |  | 425 |  |  | 345 |  |  |  | 210 |  |  |  |  | 5 |  |  | 465 |  |  |  | 510 |  |  |  |  | 210 |  |  |  | 280 |  |  |  |  | 210 |  |  |  | 200 |  |  |  | 30 | 4-φ24 |  |  |  |
| 7 |  |  |  | 1955 |  |  |  |  | 1560 |  |  |  |  | - |  |  |  |  |  | 1110 |  |  |  | 230 |  |  |  |  |  |  | 280 |  |  |  | 490 |  |  | 345 |  |  |  | 50 |  |  |  |  | 5 |  |  | 460 |  |  |  | 540 |  |  |  |  | 210 |  |  |  | 315 |  |  |  |  | 210 |  |  |  | 225 |  |  |  | 35 | 4-φ24 |  |  |  |
| 8 |  |  |  | 2135 |  |  |  |  | 1750 |  |  |  |  | - |  |  |  |  |  | 1120 |  |  |  | 390 |  |  |  |  |  |  | 280 |  |  |  | 555 |  |  | 345 |  |  |  | 260 |  |  |  |  | 5 |  |  | 480 |  |  |  | 610 |  |  |  |  | 210 |  |  |  | 330 |  |  |  |  | 210 |  |  |  | 250 |  |  |  | 30 | 4-φ24 |  |  |  |
| 9 |  |  |  | 2200 |  |  |  |  | 1750 |  |  |  |  | - |  |  |  |  |  | 1120 |  |  |  | 390 |  |  |  |  |  |  | 280 |  |  |  | 620 |  |  | 345 |  |  |  | 325 |  |  |  |  | 5 |  |  | 480 |  |  |  | 610 |  |  |  |  | 210 |  |  |  | 330 |  |  |  |  | 210 |  |  |  | 250 |  |  |  | 30 | 4-φ24 |  |  |  |
| 10 |  |  |  | 2335 |  |  |  |  | 1910 |  |  |  |  | - |  |  |  |  |  | 1240 |  |  |  | 410 |  |  |  |  |  |  | 280 |  |  |  | 685 |  |  | 345 |  |  |  | 340 |  |  |  |  | 5 |  |  | 470 |  |  |  | 660 |  |  |  |  | 210 |  |  |  | 360 |  |  |  |  | 210 |  |  |  | 280 |  |  |  | 30 | 4-φ24 |  |  |  |
| D、DM、DF、DY 46-50型泵外形安装尺寸表(共用底座) Overall installing dimension sheet(with common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 级数 |  |  |  | L |  |  |  |  | L1 |  |  |  |  | L2 |  |  |  |  |  | L3 |  |  |  | L4 |  |  |  |  |  |  | L5 |  |  |  | L6 |  |  | L7 |  |  |  | L8 |  |  |  |  | C |  |  | B1 |  |  |  | B2 |  |  |  |  | B3 |  |  |  | H |  |  |  |  | H1 |  |  |  | H2 |  |  |  | h | n-φd |  |  |  |
| 2 |  |  |  | 1682 |  |  |  |  | 1430 |  |  |  |  | - |  |  |  |  |  | 900 |  |  |  | 250 |  |  |  |  |  |  | 355 |  |  |  | 190 |  |  | 345 |  |  |  | -15 |  |  |  |  | 2 |  |  | 520 |  |  |  | 520 |  |  |  |  | 300 |  |  |  | 320 |  |  |  |  | 270 |  |  |  | 200 |  |  |  | 45 | 4-φ24 |  |  |  |
| 3 |  |  |  | 1742 |  |  |  |  | 1430 |  |  |  |  | - |  |  |  |  |  | 900 |  |  |  | 250 |  |  |  |  |  |  | 355 |  |  |  | 250 |  |  | 345 |  |  |  | 45 |  |  |  |  | 2 |  |  | 520 |  |  |  | 520 |  |  |  |  | 300 |  |  |  | 320 |  |  |  |  | 270 |  |  |  | 200 |  |  |  | 45 | 4-φ24 |  |  |  |
| 4 |  |  |  | 1842 |  |  |  |  | 1560 |  |  |  |  | 530 |  |  |  |  |  | 1060 |  |  |  | 235 |  |  |  |  |  |  | 355 |  |  |  | 310 |  |  | 345 |  |  |  | 0 |  |  |  |  | 2 |  |  | 560 |  |  |  | 560 |  |  |  |  | 300 |  |  |  | 365 |  |  |  |  | 270 |  |  |  | 225 |  |  |  | 40 | 6-φ24 |  |  |  |
| 5 |  |  |  | 2017 |  |  |  |  | 1740 |  |  |  |  | 555 |  |  |  |  |  | 1115 |  |  |  | 360 |  |  |  |  |  |  | 355 |  |  |  | 370 |  |  | 345 |  |  |  | 100 |  |  |  |  | 2 |  |  | 530 |  |  |  | 600 |  |  |  |  | 300 |  |  |  | 350 |  |  |  |  | 270 |  |  |  | 250 |  |  |  | 40 | 6-φ24 |  |  |  |
| 6 |  |  |  | 2147 |  |  |  |  | 2040 |  |  |  |  | 725 |  |  |  |  |  | 1470 |  |  |  | 380 |  |  |  |  |  |  | 355 |  |  |  | 430 |  |  | 345 |  |  |  | -30 |  |  |  |  | 2 |  |  | 500 |  |  |  | 720 |  |  |  |  | 300 |  |  |  | 430 |  |  |  |  | 270 |  |  |  | 280 |  |  |  | 40 | 6-φ24 |  |  |  |
| 7 |  |  |  | 2257 |  |  |  |  | 2040 |  |  |  |  | 725 |  |  |  |  |  | 1470 |  |  |  | 380 |  |  |  |  |  |  | 355 |  |  |  | 490 |  |  | 345 |  |  |  | 60 |  |  |  |  | 2 |  |  | 500 |  |  |  | 720 |  |  |  |  | 300 |  |  |  | 430 |  |  |  |  | 270 |  |  |  | 280 |  |  |  | 40 | 6-φ24 |  |  |  |
| 8 |  |  |  | 2317 |  |  |  |  | 2040 |  |  |  |  | 725 |  |  |  |  |  | 1470 |  |  |  | 380 |  |  |  |  |  |  | 355 |  |  |  | 550 |  |  | 345 |  |  |  | 120 |  |  |  |  | 2 |  |  | 500 |  |  |  | 720 |  |  |  |  | 300 |  |  |  | 430 |  |  |  |  | 270 |  |  |  | 280 |  |  |  | 40 | 6-φ24 |  |  |  |
| 9 |  |  |  | 2573 |  |  |  |  | 2200 |  |  |  |  | 745 |  |  |  |  |  | 1490 |  |  |  | 370 |  |  |  |  |  |  | 355 |  |  |  | 610 |  |  | 345 |  |  |  | 110 |  |  |  |  | 2 |  |  | 510 |  |  |  | 730 |  |  |  |  | 300 |  |  |  | 440 |  |  |  |  | 270 |  |  |  | 315 |  |  |  | 50 | 6-φ24 |  |  |  |
| 10 |  |  |  | 2703 |  |  |  |  | 2200 |  |  |  |  | 745 |  |  |  |  |  | 1490 |  |  |  | 370 |  |  |  |  |  |  | 355 |  |  |  | 670 |  |  | 345 |  |  |  | 170 |  |  |  |  | 2 |  |  | 510 |  |  |  | 730 |  |  |  |  | 300 |  |  |  | 440 |  |  |  |  | 270 |  |  |  | 315 |  |  |  | 50 | 6-φ24 |  |  |  |
| 11 |  |  |  | 2763 |  |  |  |  | 2200 |  |  |  |  | 745 |  |  |  |  |  | 1490 |  |  |  | 370 |  |  |  |  |  |  | 355 |  |  |  | 730 |  |  | 345 |  |  |  | 230 |  |  |  |  | 2 |  |  | 510 |  |  |  | 730 |  |  |  |  | 300 |  |  |  | 440 |  |  |  |  | 270 |  |  |  | 315 |  |  |  | 50 | 6-φ24 |  |  |  |
| 12 |  |  |  | 2823 |  |  |  |  | 2200 |  |  |  |  | 745 |  |  |  |  |  | 1490 |  |  |  | 370 |  |  |  |  |  |  | 355 |  |  |  | 790 |  |  | 345 |  |  |  | 270 |  |  |  |  | 2 |  |  | 510 |  |  |  | 730 |  |  |  |  | 300 |  |  |  | 440 |  |  |  |  | 270 |  |  |  | 315 |  |  |  | 50 | 6-φ24 |  |  |  |
| D、DM、DF、DY 85-45型泵外形安装尺寸表(共用底座) Overall installing dimension sheet(with common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 级数 |  |  |  | L |  |  |  |  | L1 |  |  |  |  | L2 |  |  |  |  |  | L3 |  |  |  | L4 |  |  |  |  |  |  | L5 |  |  |  | L6 |  |  | L7 |  |  |  | L8 |  |  |  |  | C |  |  | B1 |  |  |  | B2 |  |  |  |  | B3 |  |  |  | H |  |  |  |  | H1 |  |  |  | H2 |  |  |  | h | n-φd |  |  |  |
| 2 |  |  |  | 1641 |  |  |  |  | 1250 |  |  |  |  | - |  |  |  |  |  | 840 |  |  |  | 200 |  |  |  |  |  |  | 304 |  |  |  | 203 |  |  | 340 |  |  |  | 110 |  |  |  |  | 4 |  |  | 520 |  |  |  | 520 |  |  |  |  | 250 |  |  |  | 325 |  |  |  |  | 250 |  |  |  | 200 |  |  |  | 30 | 4-φ24 |  |  |  |
| 3 |  |  |  | 1870 |  |  |  |  | 1520 |  |  |  |  | - |  |  |  |  |  | 1040 |  |  |  | 230 |  |  |  |  |  |  | 304 |  |  |  | 277 |  |  | 340 |  |  |  | 130 |  |  |  |  | 4 |  |  | 530 |  |  |  | 635 |  |  |  |  | 250 |  |  |  | 360 |  |  |  |  | 250 |  |  |  | 250 |  |  |  | 40 | 4-φ24 |  |  |  |
| 4 |  |  |  | 2014 |  |  |  |  | 1690 |  |  |  |  | 560 |  |  |  |  |  | 1120 |  |  |  | 310 |  |  |  |  |  |  | 304 |  |  |  | 351 |  |  | 340 |  |  |  | 145 |  |  |  |  | 4 |  |  | 530 |  |  |  | 670 |  |  |  |  | 250 |  |  |  | 385 |  |  |  |  | 250 |  |  |  | 280 |  |  |  | 35 | 6-φ24 |  |  |  |
| 5 |  |  |  | 2137 |  |  |  |  | 1690 |  |  |  |  | 560 |  |  |  |  |  | 1120 |  |  |  | 310 |  |  |  |  |  |  | 304 |  |  |  | 425 |  |  | 340 |  |  |  | 205 |  |  |  |  | 4 |  |  | 520 |  |  |  | 670 |  |  |  |  | 250 |  |  |  | 385 |  |  |  |  | 250 |  |  |  | 280 |  |  |  | 35 | 6-φ24 |  |  |  |
| 本身底座without common base |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | L |  |  |  | L1 |  |  |  |  | L2 |  |  |  |  | L3 |  |  |  | L4 |  |  |  | L5 |  |  |  |  |  |  | L6 |  |  | L7 |  |  |  | L8 |  |  |  | C |  | B |  |  |  | B1 |  |  |  | B2 |  |  |  | B3 |  |  | H |  |  |  | H1 |  |  |  | H2 |  |  |  | h |  |  | n-φd |  |  |  |  | 4-φk |
| 4 |  |  | 2014 |  |  |  | 600 |  |  |  |  | 330 |  |  |  |  | 707 |  |  |  | 135 |  |  |  | 304 |  |  |  |  |  |  | 351 |  |  | 340 |  |  |  | 3 |  |  |  | 4 |  | 368 |  |  |  | 520 |  |  |  | 460 |  |  |  | 250 |  |  | 345 |  |  |  | 250 |  |  |  | 280 |  |  |  | 40 |  |  | 4-φ24 |  |  |  |  | φ24 |
| 5 |  |  | 2137 |  |  |  | 750 |  |  |  |  | 380 |  |  |  |  | 694 |  |  |  | 190 |  |  |  | 304 |  |  |  |  |  |  | 425 |  |  | 340 |  |  |  | 40 |  |  |  | 4 |  | 419 |  |  |  | 540 |  |  |  | 535 |  |  |  | 250 |  |  | 345 |  |  |  | 250 |  |  |  | 280 |  |  |  | 40 |  |  | 4-φ24 |  |  |  |  | φ24 |
| 6 |  |  | 2408 |  |  |  | 750 |  |  |  |  | 380 |  |  |  |  | 785 |  |  |  | 190 |  |  |  | 304 |  |  |  |  |  |  | 499 |  |  | 340 |  |  |  | 53 |  |  |  | 4 |  | 406 |  |  |  | 540 |  |  |  | 535 |  |  |  | 250 |  |  | 345 |  |  |  | 250 |  |  |  | 315 |  |  |  | 40 |  |  | 4-φ24 |  |  |  |  | φ28 |
| 7 |  |  | 2552 |  |  |  | 750 |  |  |  |  | 380 |  |  |  |  | 821 |  |  |  | 190 |  |  |  | 304 |  |  |  |  |  |  | 573 |  |  | 340 |  |  |  | 90 |  |  |  | 4 |  | 457 |  |  |  | 540 |  |  |  | 535 |  |  |  | 250 |  |  | 345 |  |  |  | 250 |  |  |  | 315 |  |  |  | 40 |  |  | 4-φ24 |  |  |  |  | φ28 |
| 8 |  |  | 2626 |  |  |  | 900 |  |  |  |  | 525 |  |  |  |  | 779 |  |  |  | 190 |  |  |  | 304 |  |  |  |  |  |  | 647 |  |  | 340 |  |  |  | 61 |  |  |  | 4 |  | 457 |  |  |  | 520 |  |  |  | 510 |  |  |  | 250 |  |  | 345 |  |  |  | 250 |  |  |  | 315 |  |  |  | 40 |  |  | 4-φ26 |  |  |  |  | φ28 |
| 9 |  |  | 2700 |  |  |  | 900 |  |  |  |  | 525 |  |  |  |  | 816 |  |  |  | 190 |  |  |  | 304 |  |  |  |  |  |  | 721 |  |  | 340 |  |  |  | 98 |  |  |  | 4 |  | 457 |  |  |  | 520 |  |  |  | 510 |  |  |  | 250 |  |  | 345 |  |  |  | 250 |  |  |  | 315 |  |  |  | 40 |  |  | 4-φ26 |  |  |  |  | φ28 |
| D、DM、DF、DY 85-67型泵外形安装尺寸表(本身底座) Overall installing dimension sheet(without common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | L |  | L1 |  |  |  |  | L2 |  |  |  |  | L3 |  |  |  |  |  | L4 |  | L5 |  |  |  |  |  |  | L6 |  |  |  | L7 |  |  | L8 |  |  |  | C |  |  |  | B |  |  |  | B1 |  |  |  | B2 |  |  |  | B3 |  |  | H |  |  |  | H1 |  |  | H2 |  |  |  |  | h |  | n-φd |  |  |  |  |  | 4-φk |
| 3 |  |  | 2465 |  | 765 |  |  |  |  | 400 |  |  |  |  | 880.5 |  |  |  |  |  | 182 |  | 479 |  |  |  |  |  |  | 371 |  |  |  | 559 |  |  | -14 |  |  |  | 4 |  |  |  | 419 |  |  |  | 600 |  |  |  | 457 |  |  |  | 350 |  |  | 420 |  |  |  | 350 |  |  | 280 |  |  |  |  | 50 |  | 4-φ30 |  |  |  |  |  | φ24 |
| 4 |  |  | 2743 |  | 765 |  |  |  |  | 400 |  |  |  |  | 950.5 |  |  |  |  |  | 182 |  | 479 |  |  |  |  |  |  | 459 |  |  |  | 559 |  |  | 29.5 |  |  |  | 4 |  |  |  | 406 |  |  |  | 600 |  |  |  | 508 |  |  |  | 350 |  |  | 420 |  |  |  | 350 |  |  | 315 |  |  |  |  | 60 |  | 4-φ30 |  |  |  |  |  | φ28 |
| 5 |  |  | 2901 |  | 765 |  |  |  |  | 400 |  |  |  |  | 994.5 |  |  |  |  |  | 182 |  | 479 |  |  |  |  |  |  | 547 |  |  |  | 559 |  |  | 73.5 |  |  |  | 4 |  |  |  | 457 |  |  |  | 600 |  |  |  | 508 |  |  |  | 350 |  |  | 420 |  |  |  | 350 |  |  | 315 |  |  |  |  | 60 |  | 4-φ30 |  |  |  |  |  | φ28 |
| 6 |  |  | 2989 |  | 945 |  |  |  |  | 580 |  |  |  |  | 948.5 |  |  |  |  |  | 182 |  | 479 |  |  |  |  |  |  | 635 |  |  |  | 559 |  |  | 27.5 |  |  |  | 4 |  |  |  | 457 |  |  |  | 600 |  |  |  | 508 |  |  |  | 350 |  |  | 420 |  |  |  | 350 |  |  | 315 |  |  |  |  | 50 |  | 4-φ30 |  |  |  |  |  | φ28 |
| 7 |  |  | 3007 |  | 945 |  |  |  |  | 580 |  |  |  |  | 992.5 |  |  |  |  |  | 182 |  | 479 |  |  |  |  |  |  | 723 |  |  |  | 559 |  |  | 71.5 |  |  |  | 4 |  |  |  | 457 |  |  |  | 600 |  |  |  | 508 |  |  |  | 350 |  |  | 420 |  |  |  | 350 |  |  | 315 |  |  |  |  | 50 |  | 4-φ30 |  |  |  |  |  | φ28 |
| 8 |  |  | 3395 |  | 1125 |  |  |  |  | 760 |  |  |  |  | 946.5 |  |  |  |  |  | 182 |  | 479 |  |  |  |  |  |  | 811 |  |  |  | 559 |  |  | 25.5 |  |  |  | 4 |  |  |  | 560 |  |  |  | 600 |  |  |  | 610 |  |  |  | 350 |  |  | 420 |  |  |  | 350 |  |  | 355 |  |  |  |  | 60 |  | 4-φ30 |  |  |  |  |  | φ28 |
| 9 |  |  | 3483 |  | 1125 |  |  |  |  | 760 |  |  |  |  | 990.5 |  |  |  |  |  | 182 |  | 479 |  |  |  |  |  |  | 899 |  |  |  | 559 |  |  | 69.5 |  |  |  | 4 |  |  |  | 560 |  |  |  | 600 |  |  |  | 610 |  |  |  | 350 |  |  | 420 |  |  |  | 350 |  |  | 355 |  |  |  |  | 60 |  | 4-φ30 |  |  |  |  |  | φ28 |
| D、DM、DF、DY 120-50型泵外形安装尺寸表(公用底座) Overall installing dimension sheet(with common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 级数 |  |  |  | L |  |  |  | L1 |  |  |  |  | L2 |  |  |  |  |  | L3 |  |  |  | L4 |  |  |  |  |  |  | L5 |  |  |  | L6 |  |  |  |  |  | L7 |  |  |  | L8 |  |  |  |  | C |  | B1 |  |  | B2 |  |  |  |  | B3 |  |  |  | H |  |  |  | H1 |  |  |  |  | H2 |  |  |  | h | n-φd |  |  |  |
| 2 |  |  |  | 1912 |  |  |  | 1430 |  |  |  |  | - |  |  |  |  |  | 900 |  |  |  | 265 |  |  |  |  |  |  | 304 |  |  |  | 260.5 |  |  |  |  |  | 353.5 |  |  |  | 202 |  |  |  |  | 4 |  | 595 |  |  | 595 |  |  |  |  | 300 |  |  |  | 355 |  |  |  | 1316 |  |  |  |  | 250 |  |  |  | 50 | 4-φ28 |  |  |  |
| 3 |  |  |  | 2119 |  |  |  | 1635 |  |  |  |  | - |  |  |  |  |  | 1000 |  |  |  | 300 |  |  |  |  |  |  | 304 |  |  |  | 347.5 |  |  |  |  |  | 353.5 |  |  |  | 237 |  |  |  |  | 4 |  | 545 |  |  | 650 |  |  |  |  | 300 |  |  |  | 385 |  |  |  | 1316 |  |  |  |  | 280 |  |  |  | 50 | 4-φ28 |  |  |  |
| 4 |  |  |  | 2466 |  |  |  | 1895 |  |  |  |  | 500 |  |  |  |  |  | 1200 |  |  |  | 300 |  |  |  |  |  |  | 304 |  |  |  | 434.5 |  |  |  |  |  | 353.5 |  |  |  | 237 |  |  |  |  | 4 |  | 550 |  |  | 735 |  |  |  |  | 300 |  |  |  | 435 |  |  |  | 1316 |  |  |  |  | 315 |  |  |  | 50 | 6-φ40 |  |  |  |
| 5 |  |  |  | 2253 |  |  |  | 1895 |  |  |  |  | 500 |  |  |  |  |  | 1200 |  |  |  | 300 |  |  |  |  |  |  | 304 |  |  |  | 521.5 |  |  |  |  |  | 353.5 |  |  |  | 237 |  |  |  |  | 4 |  | 550 |  |  | 735 |  |  |  |  | 300 |  |  |  | 435 |  |  |  | 1316 |  |  |  |  | 315 |  |  |  | 50 | 6-φ40 |  |  |  |
| 6 |  |  |  | 2640 |  |  |  | 2210 |  |  |  |  | 550 |  |  |  |  |  | 1350 |  |  |  | 400 |  |  |  |  |  |  | 304 |  |  |  | 608.5 |  |  |  |  |  | 353.5 |  |  |  | 337 |  |  |  |  | 4 |  | 550 |  |  | 750 |  |  |  |  | 300 |  |  |  | 435 |  |  |  | 1316 |  |  |  |  | 315 |  |  |  | 50 | 6-φ40 |  |  |  |
| 7 |  |  |  | 2727 |  |  |  | 2210 |  |  |  |  | 550 |  |  |  |  |  | 1350 |  |  |  | 400 |  |  |  |  |  |  | 304 |  |  |  | 695.5 |  |  |  |  |  | 353.5 |  |  |  | 337 |  |  |  |  | 4 |  | 550 |  |  | 750 |  |  |  |  | 300 |  |  |  | 435 |  |  |  | 1316 |  |  |  |  | 315 |  |  |  | 50 | 6-φ40 |  |  |  |
| 8 |  |  |  | 2814 |  |  |  | 2210 |  |  |  |  | 550 |  |  |  |  |  | 1350 |  |  |  | 400 |  |  |  |  |  |  | 304 |  |  |  | 782.5 |  |  |  |  |  | 353.5 |  |  |  | 337 |  |  |  |  | 4 |  | 550 |  |  | 750 |  |  |  |  | 300 |  |  |  | 435 |  |  |  | 1316 |  |  |  |  | 315 |  |  |  | 50 | 6-φ40 |  |  |  |
| 9 |  |  |  | 2901 |  |  |  | 2370 |  |  |  |  | 800 |  |  |  |  |  | 1600 |  |  |  | 400 |  |  |  |  |  |  | 304 |  |  |  | 869.5 |  |  |  |  |  | 353.5 |  |  |  | 337 |  |  |  |  | 4 |  | 550 |  |  | 860 |  |  |  |  | 300 |  |  |  | 485 |  |  |  | 1315 |  |  |  |  | 355 |  |  |  | 50 | 6-φ40 |  |  |  |
| D、DM、DF、DY 155-30型泵外形安装尺寸表(公用底座) Overall installing dimension sheet(with common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 级数 |  |  |  | L |  |  |  | L1 |  |  |  |  | L2 |  |  |  |  |  | L3 |  |  |  | L4 |  |  |  |  |  |  | L5 |  |  |  | L6 |  |  |  |  |  | L7 |  |  |  | L8 |  |  |  |  | C |  | B1 |  |  | B2 |  |  |  |  | B3 |  |  |  | H |  |  |  | H1 |  |  |  |  | H2 |  |  |  | h | n-φd |  |  |  |
| 2 |  |  |  | 1916 |  |  |  | 1980 |  |  |  |  | 680 |  |  |  |  |  | 1350 |  |  |  | 315 |  |  |  |  |  |  | 365 |  |  |  | 310 |  |  |  |  |  | 388 |  |  |  | -25 |  |  |  |  | 4 |  | 660 |  |  | 660 |  |  |  |  | 350 |  |  |  | 400 |  |  |  | 350 |  |  |  |  | 225 |  |  |  | 35 | 6-φ26 |  |  |  |
| 3 |  |  |  | 2186 |  |  |  | 1980 |  |  |  |  | 680 |  |  |  |  |  | 1350 |  |  |  | 315 |  |  |  |  |  |  | 365 |  |  |  | 425 |  |  |  |  |  | 388 |  |  |  | 90 |  |  |  |  | 4 |  | 660 |  |  | 660 |  |  |  |  | 350 |  |  |  | 400 |  |  |  | 350 |  |  |  |  | 280 |  |  |  | 35 | 6-φ26 |  |  |  |
| 4 |  |  |  | 2351 |  |  |  | 1980 |  |  |  |  | 680 |  |  |  |  |  | 1350 |  |  |  | 315 |  |  |  |  |  |  | 365 |  |  |  | 540 |  |  |  |  |  | 388 |  |  |  | 210 |  |  |  |  | 4 |  | 660 |  |  | 660 |  |  |  |  | 350 |  |  |  | 400 |  |  |  | 350 |  |  |  |  | 280 |  |  |  | 35 | 6-φ26 |  |  |  |
| 5 |  |  |  | 2710 |  |  |  | 2400 |  |  |  |  | 750 |  |  |  |  |  | 1500 |  |  |  | 530 |  |  |  |  |  |  | 365 |  |  |  | 655 |  |  |  |  |  | 418 |  |  |  | 230 |  |  |  |  | 4 |  | 580 |  |  | 720 |  |  |  |  | 350 |  |  |  | 445 |  |  |  | 350 |  |  |  |  | 315 |  |  |  | 35 | 6-φ26 |  |  |  |
| 6 |  |  |  | 2897 |  |  |  | 2400 |  |  |  |  | 750 |  |  |  |  |  | 1500 |  |  |  | 530 |  |  |  |  |  |  | 365 |  |  |  | 770 |  |  |  |  |  | 418 |  |  |  | 345 |  |  |  |  | 4 |  | 580 |  |  | 720 |  |  |  |  | 350 |  |  |  | 445 |  |  |  | 350 |  |  |  |  | 315 |  |  |  | 35 | 6-φ26 |  |  |  |
| 7 |  |  |  | 3014 |  |  |  | 2400 |  |  |  |  | 750 |  |  |  |  |  | 1500 |  |  |  | 530 |  |  |  |  |  |  | 365 |  |  |  | 885 |  |  |  |  |  | 418 |  |  |  | 460 |  |  |  |  | 4 |  | 580 |  |  | 720 |  |  |  |  | 350 |  |  |  | 445 |  |  |  | 350 |  |  |  |  | 315 |  |  |  | 35 | 6-φ26 |  |  |  |
| D、DM、DF、DY本身底座 Without common base |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | L |  |  |  | L1 |  |  |  |  | L2 |  |  |  |  |  |  |  | L3 |  |  | L4 |  | L5 |  |  |  |  |  |  | L6 |  |  |  | L7 |  | L8 |  |  |  |  | C |  |  |  | B |  |  |  | B1 |  |  |  | B2 |  |  |  | B3 |  |  | H |  |  |  | H1 |  |  | H2 |  |  |  |  | h |  | n-φd |  |  |  |  |  | 4-φk |
| 2 | 1916 |  |  |  | 740 |  |  |  |  | 450 |  |  |  |  |  |  |  | 605 |  |  | 140 |  | 365 |  |  |  |  |  |  | 310 |  |  |  | 388 |  | -70 |  |  |  |  | 4 |  |  |  | 311 |  |  |  | 356 |  |  |  | 356 |  |  |  | 350 |  |  | 400 |  |  |  | 350 |  |  | 225 |  |  |  |  | 50 |  | 4-φ26 |  |  |  |  |  | φ24 |
| 3 | 2186 |  |  |  | 740 |  |  |  |  | 450 |  |  |  |  |  |  |  | 746 |  |  | 140 |  | 365 |  |  |  |  |  |  | 425 |  |  |  | 388 |  | -12.5 |  |  |  |  | 4 |  |  |  | 368 |  |  |  | 457 |  |  |  | 457 |  |  |  | 350 |  |  | 400 |  |  |  | 350 |  |  | 280 |  |  |  |  | 50 |  | 4-φ26 |  |  |  |  |  | φ24 |
| 4 | 2351 |  |  |  | 740 |  |  |  |  | 450 |  |  |  |  |  |  |  | 804 |  |  | 140 |  | 365 |  |  |  |  |  |  | 540 |  |  |  | 388 |  | 45 |  |  |  |  | 4 |  |  |  | 419 |  |  |  | 457 |  |  |  | 457 |  |  |  | 350 |  |  | 400 |  |  |  | 350 |  |  | 280 |  |  |  |  | 50 |  | 4-φ26 |  |  |  |  |  | φ24 |
| 5 | 2710 |  |  |  | 1060 |  |  |  |  | 805 |  |  |  |  |  |  |  | 811 |  |  | 140 |  | 365 |  |  |  |  |  |  | 655 |  |  |  | 418 |  | 70 |  |  |  |  | 4 |  |  |  | 406 |  |  |  | 508 |  |  |  | 508 |  |  |  | 350 |  |  | 400 |  |  |  | 350 |  |  | 315 |  |  |  |  | 40 |  | 4-φ27 |  |  |  |  |  | φ28 |
| 6 | 2897 |  |  |  | 1060 |  |  |  |  | 805 |  |  |  |  |  |  |  | 868 |  |  | 140 |  | 365 |  |  |  |  |  |  | 770 |  |  |  | 418 |  | 12.5 |  |  |  |  | 4 |  |  |  | 457 |  |  |  | 508 |  |  |  | 508 |  |  |  | 350 |  |  | 400 |  |  |  | 350 |  |  | 315 |  |  |  |  | 40 |  | 4-φ27 |  |  |  |  |  | φ28 |
| 7 | 3014 |  |  |  | 1060 |  |  |  |  | 805 |  |  |  |  |  |  |  | 958 |  |  | 140 |  | 365 |  |  |  |  |  |  | 885 |  |  |  | 418 |  | -45 |  |  |  |  | 4 |  |  |  | 457 |  |  |  | 508 |  |  |  | 508 |  |  |  | 350 |  |  | 400 |  |  |  | 350 |  |  | 315 |  |  |  |  | 40 |  | 4-φ27 |  |  |  |  |  | φ28 |
| 8 | 3130 |  |  |  | 1500 |  |  |  |  | 1210 |  |  |  |  |  |  |  | 821 |  |  | 145 |  | 365 |  |  |  |  |  |  | 1000 |  |  |  | 418 |  | -105 |  |  |  |  | 4 |  |  |  | 508 |  |  |  | 508 |  |  |  | 508 |  |  |  | 350 |  |  | 400 |  |  |  | 350 |  |  | 315 |  |  |  |  | 40 |  | 4-φ25 |  |  |  |  |  | φ28 |
| 9 | 3245 |  |  |  | 1500 |  |  |  |  | 1210 |  |  |  |  |  |  |  | 878 |  |  | 145 |  | 365 |  |  |  |  |  |  | 1115 |  |  |  | 418 |  | -47.5 |  |  |  |  | 5 |  |  |  | 508 |  |  |  | 508 |  |  |  | 508 |  |  |  | 350 |  |  | 400 |  |  |  | 350 |  |  | 315 |  |  |  |  | 40 |  | 4-φ25 |  |  |  |  |  | φ28 |
| 10 | 3590 |  |  |  | 1500 |  |  |  |  | 1210 |  |  |  |  |  |  |  | 903 |  |  | 145 |  | 365 |  |  |  |  |  |  | 1230 |  |  |  | 418 |  | 10 |  |  |  |  | 5 |  |  |  | 560 |  |  |  | 560 |  |  |  | 610 |  |  |  | 350 |  |  | 400 |  |  |  | 350 |  |  | 355 |  |  |  |  | 40 |  | 4-φ25 |  |  |  |  |  | φ28 |
| D、DM、DF、DY 155-67型泵外形安装尺寸表(本身底座) Overall installing dimension sheet(without common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | L |  |  |  | L1 |  |  |  |  | L2 |  |  |  |  |  |  |  | L3 |  |  |  | L4 |  |  |  | L5 |  | L6 |  |  |  |  |  | L7 |  | L8 |  |  |  |  |  | C |  |  | B |  |  |  | B1 |  |  |  | B2 |  |  |  | B3 |  |  | H |  |  |  | H1 |  |  |  | H2 |  |  |  | h |  | n-φd |  |  |  |  |  | 4-φk |
| 3 | 2725 |  |  |  | 765 |  |  |  |  | 400 |  |  |  |  |  |  |  | 906.5 |  |  |  | 182 |  |  |  | 479 |  | 371 |  |  |  |  |  | 559 |  | -14 |  |  |  |  |  | 4 |  |  | 457 |  |  |  | 600 |  |  |  | 508 |  |  |  | 355 |  |  | 420 |  |  |  | 350 |  |  |  | 315 |  |  |  | 50 |  | 4-φ30 |  |  |  |  |  | φ28 |
| 4 | 2743 |  |  |  | 765 |  |  |  |  | 400 |  |  |  |  |  |  |  | 950.5 |  |  |  | 182 |  |  |  | 479 |  | 45 |  |  |  |  |  | 559 |  | 29.5 |  |  |  |  |  | 4 |  |  | 457 |  |  |  | 600 |  |  |  | 508 |  |  |  | 355 |  |  | 420 |  |  |  | 350 |  |  |  | 315 |  |  |  | 50 |  | 4-φ30 |  |  |  |  |  | φ28 |
| 5 | 3131 |  |  |  | 765 |  |  |  |  | 400 |  |  |  |  |  |  |  | 995.5 |  |  |  | 182 |  |  |  | 479 |  | 547 |  |  |  |  |  | 559 |  | 73.5 |  |  |  |  |  | 4 |  |  | 560 |  |  |  | 600 |  |  |  | 610 |  |  |  | 355 |  |  | 420 |  |  |  | 350 |  |  |  | 355 |  |  |  | 50 |  | 4-φ30 |  |  |  |  |  | φ28 |
| 6 | 3219 |  |  |  | 945 |  |  |  |  | 580 |  |  |  |  |  |  |  | 987.5 |  |  |  | 182 |  |  |  | 479 |  | 635 |  |  |  |  |  | 559 |  | 27.5 |  |  |  |  |  | 4 |  |  | 630 |  |  |  | 600 |  |  |  | 610 |  |  |  | 355 |  |  | 420 |  |  |  | 350 |  |  |  | 355 |  |  |  | 50 |  | 4-φ30 |  |  |  |  |  | φ28 |
| 7 | 3308 |  |  |  | 945 |  |  |  |  | 580 |  |  |  |  |  |  |  | 1031 |  |  |  | 182 |  |  |  | 479 |  | 723 |  |  |  |  |  | 559 |  | 71.5 |  |  |  |  |  | 5 |  |  | 630 |  |  |  | 600 |  |  |  | 610 |  |  |  | 355 |  |  | 420 |  |  |  | 350 |  |  |  | 355 |  |  |  | 50 |  | 4-φ30 |  |  |  |  |  | φ28 |
| 8 | 3295 |  |  |  | 1125 |  |  |  |  | 760 |  |  |  |  |  |  |  | 985.5 |  |  |  | 182 |  |  |  | 479 |  | 811 |  |  |  |  |  | 559 |  | 25.5 |  |  |  |  |  | 5 |  |  | 630 |  |  |  | 600 |  |  |  | 610 |  |  |  | 355 |  |  | 420 |  |  |  | 350 |  |  |  | 355 |  |  |  | 50 |  | 4-φ30 |  |  |  |  |  | φ28 |
| 9 | 4634 |  |  |  | 1125 |  |  |  |  | 760 |  |  |  |  |  |  |  | 1095 |  |  |  | 182 |  |  |  | 479 |  | 899 |  |  |  |  |  | 559 |  | 69.5 |  |  |  |  |  | 5 |  |  | 1000 |  |  |  | 600 |  |  |  | 710 |  |  |  | 355 |  |  | 420 |  |  |  | 350 |  |  |  | 400 |  |  |  | 50 |  | 4-φ30 |  |  |  |  |  | φ32 |
| D、DM、DF、DY 280-43型泵外形安装尺寸表(本身底座) Overall installing dimension sheet(without common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | L |  |  |  | L1 |  |  |  |  | L2 |  |  |  |  | L3 |  |  |  |  |  |  | L4 |  |  |  | L5 |  | L6 |  |  |  |  |  | L7 |  | L8 |  |  |  |  |  | C |  |  | B |  |  |  | B1 |  |  |  | B2 |  |  | B3 |  |  | H |  |  | H1 |  |  |  | H2 |  |  |  | h |  | h1 |  | n-φd |  |  |  |  |  | 4-φk |
| 2 | 2423 |  |  |  | 735 |  |  |  |  | 435 |  |  |  |  | 773 |  |  |  |  |  |  | 150 |  |  |  | 384 |  | 373 |  |  |  |  |  | 388 |  | -52 |  |  |  |  |  | 5 |  |  | 406 |  |  |  | 700 |  |  |  | 508 |  |  | 450 |  |  | 480 |  |  | 400 |  |  |  | 315 |  |  |  | 50 |  | 35 |  | 4-φ30 |  |  |  |  |  | φ28 |
| 3 | 2623 |  |  |  | 735 |  |  |  |  | 435 |  |  |  |  | 838 |  |  |  |  |  |  | 150 |  |  |  | 384 |  | 503 |  |  |  |  |  | 388 |  | 13 |  |  |  |  |  | 5 |  |  | 457 |  |  |  | 700 |  |  |  | 508 |  |  | 450 |  |  | 480 |  |  | 400 |  |  |  | 315 |  |  |  | 50 |  | 35 |  | 4-φ30 |  |  |  |  |  | φ28 |
| 4 | 2753 |  |  |  | 735 |  |  |  |  | 435 |  |  |  |  | 903 |  |  |  |  |  |  | 150 |  |  |  | 384 |  | 633 |  |  |  |  |  | 388 |  | 78 |  |  |  |  |  | 5 |  |  | 508 |  |  |  | 700 |  |  |  | 508 |  |  | 450 |  |  | 480 |  |  | 400 |  |  |  | 315 |  |  |  | 50 |  | 38 |  | 4-φ30 |  |  |  |  |  | φ28 |
| 5 | 3113 |  |  |  | 1125 |  |  |  |  | 800 |  |  |  |  | 821.5 |  |  |  |  |  |  | 162.5 |  |  |  | 384 |  | 763 |  |  |  |  |  | 388 |  | -39.5 |  |  |  |  |  | 5 |  |  | 560 |  |  |  | 700 |  |  |  | 610 |  |  | 450 |  |  | 480 |  |  | 400 |  |  |  | 355 |  |  |  | 50 |  | 38 |  | 4-φ30 |  |  |  |  |  | φ28 |
| 6 | 3243 |  |  |  | 1125 |  |  |  |  | 800 |  |  |  |  | 886.5 |  |  |  |  |  |  | 162.5 |  |  |  | 384 |  | 893 |  |  |  |  |  | 388 |  | 25.5 |  |  |  |  |  | 5 |  |  | 630 |  |  |  | 700 |  |  |  | 610 |  |  | 450 |  |  | 480 |  |  | 400 |  |  |  | 355 |  |  |  | 50 |  | 38 |  | 4-φ30 |  |  |  |  |  | φ28 |
| 7 | 3815 |  |  |  | 1125 |  |  |  |  | 800 |  |  |  |  | 1072.5 |  |  |  |  |  |  | 162.5 |  |  |  | 384 |  | 1023 |  |  |  |  |  | 420 |  | 90.5 |  |  |  |  |  | 6 |  |  | 1000 |  |  |  | 700 |  |  |  | 710 |  |  | 450 |  |  | 480 |  |  | 400 |  |  |  | 400 |  |  |  | 50 |  | 38 |  | 4-φ30 |  |  |  |  |  | φ35 |
| 8 | 3945 |  |  |  | 1385 |  |  |  |  | 1060 |  |  |  |  | 1007.5 |  |  |  |  |  |  | 162.5 |  |  |  | 384 |  | 1153 |  |  |  |  |  | 420 |  | 25.5 |  |  |  |  |  | 6 |  |  | 1000 |  |  |  | 700 |  |  |  | 710 |  |  | 450 |  |  | 480 |  |  | 400 |  |  |  | 400 |  |  |  | 50 |  | 38 |  | 4-φ30 |  |  |  |  |  | φ35 |
| 9 | 4075 |  |  |  | 1385 |  |  |  |  | 1060 |  |  |  |  | 1072.5 |  |  |  |  |  |  | 162.5 |  |  |  | 384 |  | 1283 |  |  |  |  |  | 420 |  | 90.5 |  |  |  |  |  | 6 |  |  | 1000 |  |  |  | 700 |  |  |  | 710 |  |  | 450 |  |  | 480 |  |  | 400 |  |  |  | 400 |  |  |  | 50 |  | 38 |  | 4-φ30 |  |  |  |  |  | φ35 |
| D、DM、DF、DY 280-65型泵外形安装尺寸表(本身底座) Overall installing dimension sheet(without common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | L |  |  |  | L1 |  |  |  |  | L2 |  |  |  |  | L3 |  |  |  |  |  |  | L4 |  |  |  | L5 |  | L6 |  |  |  |  |  | L7 |  | L8 |  |  |  |  |  | C |  |  | B |  |  |  | B1 |  |  |  | B2 |  |  | B3 |  |  | H |  |  | H1 |  |  |  | H2 |  |  |  | h |  | h1 |  | n-φd |  |  |  |  |  | 4-φk |
| 3 | 3214 |  |  |  | 690 |  |  |  |  | 310 |  |  |  |  | 1243 |  |  |  |  |  |  | 190 |  |  |  | 536 |  | 475 |  |  |  |  |  | 625 |  | 80 |  |  |  |  |  | 6 |  |  | 900 |  |  |  | 790 |  |  |  | 630 |  |  | 500 |  |  | 530 |  |  | 500 |  |  |  | 355 |  |  |  | 50 |  | 35 |  | 4-φ40 |  |  |  |  |  | φ28 |
| 4 | 3754 |  |  |  | 820 |  |  |  |  | 440 |  |  |  |  | 1263 |  |  |  |  |  |  | 190 |  |  |  | 536 |  | 605 |  |  |  |  |  | 625 |  | 80 |  |  |  |  |  | 6 |  |  | 1000 |  |  |  | 790 |  |  |  | 710 |  |  | 500 |  |  | 530 |  |  | 500 |  |  |  | 400 |  |  |  | 50 |  | 38 |  | 4-φ40 |  |  |  |  |  | φ35 |
| 5 | 3884 |  |  |  | 950 |  |  |  |  | 570 |  |  |  |  | 1263 |  |  |  |  |  |  | 190 |  |  |  | 536 |  | 735 |  |  |  |  |  | 625 |  | 80 |  |  |  |  |  | 6 |  |  | 1000 |  |  |  | 790 |  |  |  | 710 |  |  | 500 |  |  | 530 |  |  | 500 |  |  |  | 400 |  |  |  | 50 |  | 38 |  | 4-φ40 |  |  |  |  |  | φ35 |
| 6 | 4014 |  |  |  | 1080 |  |  |  |  | 700 |  |  |  |  | 1284 |  |  |  |  |  |  | 190 |  |  |  | 536 |  | 865 |  |  |  |  |  | 625 |  | 80 |  |  |  |  |  | 7 |  |  | 1000 |  |  |  | 790 |  |  |  | 710 |  |  | 500 |  |  | 530 |  |  | 500 |  |  |  | 400 |  |  |  | 50 |  | 38 |  | 4-φ40 |  |  |  |  |  | φ35 |
| 7 | 4345 |  |  |  | 1210 |  |  |  |  | 830 |  |  |  |  | 1284 |  |  |  |  |  |  | 190 |  |  |  | 536 |  | 995 |  |  |  |  |  | 625 |  | 80 |  |  |  |  |  | 7 |  |  | 1120 |  |  |  | 790 |  |  |  | 800 |  |  | 500 |  |  | 530 |  |  | 500 |  |  |  | 450 |  |  |  | 50 |  | 38 |  | 4-φ40 |  |  |  |  |  | φ35 |
| 8 | 4475 |  |  |  | 1340 |  |  |  |  | 960 |  |  |  |  | 1284 |  |  |  |  |  |  | 190 |  |  |  | 536 |  | 1125 |  |  |  |  |  | 625 |  | 80 |  |  |  |  |  | 7 |  |  | 1120 |  |  |  | 790 |  |  |  | 800 |  |  | 500 |  |  | 530 |  |  | 500 |  |  |  | 450 |  |  |  | 50 |  | 38 |  | 4-φ40 |  |  |  |  |  | φ35 |
| 9 | 4605 |  |  |  | 1470 |  |  |  |  | 1090 |  |  |  |  | 1284 |  |  |  |  |  |  | 190 |  |  |  | 536 |  | 1255 |  |  |  |  |  | 625 |  | 80 |  |  |  |  |  | 7 |  |  | 1120 |  |  |  | 790 |  |  |  | 800 |  |  | 500 |  |  | 530 |  |  | 500 |  |  |  | 450 |  |  |  | 50 |  | 38 |  | 4-φ40 |  |  |  |  |  | φ35 |
| 10 | 5105 |  |  |  | 1600 |  |  |  |  | 1220 |  |  |  |  | 1444 |  |  |  |  |  |  | 190 |  |  |  | 536 |  | 1385 |  |  |  |  |  | 625 |  | 80 |  |  |  |  |  | 7 |  |  | 1120 |  |  |  | 790 |  |  |  | 800 |  |  | 500 |  |  | 530 |  |  | 500 |  |  |  | 450 |  |  |  | 50 |  | 38 |  | 4-φ40 |  |  |  |  |  | φ35 |
| D、DM、DF、DY280-80型泵外形安装尺寸表(本身底座) Overall installing dimension sheet(without common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | L |  |  |  | L1 |  |  |  |  | L2 |  |  |  |  |  |  |  | L3 |  |  |  | L4 |  |  |  | L5 |  | L6 |  |  |  |  |  | L7 |  | L8 |  |  |  |  |  | C |  |  | B |  |  |  | B1 |  |  |  | B2 |  |  |  | B3 |  |  | H |  |  |  | H1 |  |  | H2 |  |  |  |  | h |  | n-φd |  |  |  | 4-φk |  |  |
| 6 | 4065 |  |  |  | 1225 |  |  |  |  | 845 |  |  |  |  |  |  |  | 1211 |  |  |  | 190 |  |  |  | 510 |  | 915 |  |  |  |  |  | 600 |  | 30 |  |  |  |  |  | 6 |  |  | 1120 |  |  |  | 970 |  |  |  | 800 |  |  |  | 600 |  |  | 690 |  |  |  | 600 |  |  | 450 |  |  |  |  | 50 |  | 4-φ35 |  |  |  | φ35 |  |  |
| 7 | 4200 |  |  |  | 1360 |  |  |  |  | 980 |  |  |  |  |  |  |  | 1211 |  |  |  | 190 |  |  |  | 510 |  | 1050 |  |  |  |  |  | 600 |  | 30 |  |  |  |  |  | 6 |  |  | 1120 |  |  |  | 970 |  |  |  | 800 |  |  |  | 600 |  |  | 690 |  |  |  | 600 |  |  | 450 |  |  |  |  | 50 |  | 4-φ35 |  |  |  | φ35 |  |  |
| 8 | 4335 |  |  |  | 1495 |  |  |  |  | 1115 |  |  |  |  |  |  |  | 1211 |  |  |  | 190 |  |  |  | 510 |  | 1185 |  |  |  |  |  | 600 |  | 30 |  |  |  |  |  | 6 |  |  | 1120 |  |  |  | 970 |  |  |  | 800 |  |  |  | 600 |  |  | 690 |  |  |  | 600 |  |  | 450 |  |  |  |  | 50 |  | 4-φ35 |  |  |  | φ35 |  |  |
| 9 | 4637 |  |  |  | 1630 |  |  |  |  | 1250 |  |  |  |  |  |  |  | 1365 |  |  |  | 190 |  |  |  | 510 |  | 1320 |  |  |  |  |  | 600 |  | 30 |  |  |  |  |  | 6 |  |  | 1250 |  |  |  | 970 |  |  |  | 900 |  |  |  | 600 |  |  | 690 |  |  |  | 600 |  |  | 500 |  |  |  |  | 50 |  | 4-φ35 |  |  |  | φ42 |  |  |
| 10 | 4772 |  |  |  | 1765 |  |  |  |  | 1385 |  |  |  |  |  |  |  | 1365 |  |  |  | 190 |  |  |  | 510 |  | 1455 |  |  |  |  |  | 600 |  | 30 |  |  |  |  |  | 6 |  |  | 1250 |  |  |  | 970 |  |  |  | 900 |  |  |  | 600 |  |  | 690 |  |  |  | 600 |  |  | 500 |  |  |  |  | 50 |  | 4-φ35 |  |  |  | φ42 |  |  |
| 11 | 4907 |  |  |  | 1900 |  |  |  |  | 1520 |  |  |  |  |  |  |  | 1365 |  |  |  | 190 |  |  |  | 510 |  | 1590 |  |  |  |  |  | 600 |  | 30 |  |  |  |  |  | 6 |  |  | 1250 |  |  |  | 970 |  |  |  | 900 |  |  |  | 600 |  |  | 690 |  |  |  | 600 |  |  | 500 |  |  |  |  | 50 |  | 4-φ35 |  |  |  | φ42 |  |  |
| 12 | 5042 |  |  |  | 2035 |  |  |  |  | 1655 |  |  |  |  |  |  |  | 1365 |  |  |  | 190 |  |  |  | 510 |  | 1725 |  |  |  |  |  | 600 |  | 30 |  |  |  |  |  | 6 |  |  | 1250 |  |  |  | 970 |  |  |  | 900 |  |  |  | 600 |  |  | 690 |  |  |  | 600 |  |  | 500 |  |  |  |  | 50 |  | 4-φ35 |  |  |  | φ42 |  |  |
| D、DM、DF、DY 280-100型泵外形安装尺寸表(本身底座) Overall installing dimension sheet(without common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | L |  |  |  | L1 |  |  |  |  | L2 |  |  |  |  | L3 |  |  |  |  |  |  | L4 |  |  |  | L5 |  | L6 |  |  |  |  |  | L7 |  | L8 |  |  |  |  |  | C |  |  | B |  |  |  | B1 |  |  |  | B2 |  |  | B3 |  |  | H |  |  | H1 |  |  |  | H2 |  |  |  | h |  | h1 |  | n-φd |  |  |  |  |  | 4-φk |
| 4 | 3788 |  |  |  | 815 |  |  |  |  | 455 |  |  |  |  | 1098 |  |  |  |  |  |  | 180 |  |  |  | 669 |  | 600 |  |  |  |  |  | 513 |  | 100 |  |  |  |  |  | 6 |  |  | 1000 |  |  |  | 875 |  |  |  | 710 |  |  | 500 |  |  | 1050 |  |  | 754 |  |  |  | 400 |  |  |  | 50 |  | 40 |  | 4-φ35 |  |  |  |  |  | φ35 |
| 5 | 3948 |  |  |  | 1055 |  |  |  |  | 695 |  |  |  |  | 1073 |  |  |  |  |  |  | 180 |  |  |  | 669 |  | 720 |  |  |  |  |  | 513 |  | -20 |  |  |  |  |  | 6 |  |  | 1250 |  |  |  | 875 |  |  |  | 900 |  |  | 500 |  |  | 1050 |  |  | 754 |  |  |  | 450 |  |  |  | 50 |  | 40 |  | 4-φ35 |  |  |  |  |  | φ35 |
| 6 | 4068 |  |  |  | 1055 |  |  |  |  | 695 |  |  |  |  | 1133 |  |  |  |  |  |  | 180 |  |  |  | 669 |  | 840 |  |  |  |  |  | 513 |  | 100 |  |  |  |  |  | 6 |  |  | 1250 |  |  |  | 875 |  |  |  | 900 |  |  | 500 |  |  | 1050 |  |  | 754 |  |  |  | 450 |  |  |  | 50 |  | 40 |  | 4-φ35 |  |  |  |  |  | φ35 |
| 7 | 4188 |  |  |  | 1195 |  |  |  |  | 835 |  |  |  |  | 1123 |  |  |  |  |  |  | 180 |  |  |  | 669 |  | 960 |  |  |  |  |  | 513 |  | 80 |  |  |  |  |  | 6 |  |  | 1250 |  |  |  | 875 |  |  |  | 900 |  |  | 500 |  |  | 1050 |  |  | 754 |  |  |  | 450 |  |  |  | 50 |  | 40 |  | 4-φ35 |  |  |  |  |  | φ35 |
| 8 | 4475 |  |  |  | 1195 |  |  |  |  | 835 |  |  |  |  | 1283 |  |  |  |  |  |  | 180 |  |  |  | 669 |  | 1080 |  |  |  |  |  | 513 |  | 280 |  |  |  |  |  | 6 |  |  | 1250 |  |  |  | 875 |  |  |  | 900 |  |  | 500 |  |  | 1050 |  |  | 754 |  |  |  | 500 |  |  |  | 50 |  | 40 |  | 4-φ35 |  |  |  |  |  | φ42 |
| 9 | 4595 |  |  |  | 1535 |  |  |  |  | 1175 |  |  |  |  | 1173 |  |  |  |  |  |  | 180 |  |  |  | 669 |  | 1200 |  |  |  |  |  | 513 |  | -20 |  |  |  |  |  | 6 |  |  | 1250 |  |  |  | 875 |  |  |  | 900 |  |  | 500 |  |  | 1050 |  |  | 754 |  |  |  | 500 |  |  |  | 50 |  | 40 |  | 4-φ35 |  |  |  |  |  | φ42 |
| 10 | 4715 |  |  |  | 1535 |  |  |  |  | 1175 |  |  |  |  | 1233 |  |  |  |  |  |  | 180 |  |  |  | 669 |  | 1320 |  |  |  |  |  | 513 |  | 100 |  |  |  |  |  | 6 |  |  | 1250 |  |  |  | 875 |  |  |  | 900 |  |  | 500 |  |  | 1050 |  |  | 754 |  |  |  | 500 |  |  |  | 50 |  | 40 |  | 4-φ35 |  |  |  |  |  | φ42 |
| DM、DF、DY 360-40型泵外形安装尺寸表(本身底座) Overall installing dimension sheet(without common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | L |  |  |  | L1 |  |  |  |  | L2 |  |  |  |  | L3 |  |  |  |  |  | L4 |  |  |  |  | L5 |  | L6 |  |  |  | L7 |  |  | L8 |  |  |  |  |  | C |  |  |  | B |  | B1 |  |  |  | B2 |  |  | B3 |  |  | H |  |  | H1 |  |  |  | H2 |  |  |  | h |  | h1 |  | n-φd |  |  |  |  |  | 4-φk |  |
| 2 |  | 2539 |  |  |  | 505 |  |  |  |  | 200 |  |  |  |  | 927 |  |  |  |  |  | 150 |  |  |  |  | 384 |  | 390 |  |  |  | 417 |  |  | 73 |  |  |  |  |  | 6 |  |  |  | 457 |  | 700 |  |  |  | 508 |  |  | 450 |  |  | 450 |  |  | 400 |  |  |  | 315 |  |  |  | 50 |  | 38 |  | 4-φ40 |  |  |  |  |  | φ28 |  |
| 3 |  | 2909 |  |  |  | 645 |  |  |  |  | 340 |  |  |  |  | 965 |  |  |  |  |  | 150 |  |  |  |  | 384 |  | 530 |  |  |  | 417 |  |  | 73 |  |  |  |  |  | 6 |  |  |  | 560 |  | 700 |  |  |  | 610 |  |  | 450 |  |  | 450 |  |  | 400 |  |  |  | 355 |  |  |  | 50 |  | 38 |  | 4-φ40 |  |  |  |  |  | φ28 |  |
| 4 |  | 3049 |  |  |  | 785 |  |  |  |  | 480 |  |  |  |  | 965 |  |  |  |  |  | 150 |  |  |  |  | 384 |  | 670 |  |  |  | 417 |  |  | 73 |  |  |  |  |  | 6 |  |  |  | 560 |  | 700 |  |  |  | 610 |  |  | 450 |  |  | 450 |  |  | 400 |  |  |  | 355 |  |  |  | 50 |  | 38 |  | 4-φ40 |  |  |  |  |  | φ28 |  |
| 5 |  | 3189 |  |  |  | 925 |  |  |  |  | 620 |  |  |  |  | 965 |  |  |  |  |  | 150 |  |  |  |  | 384 |  | 810 |  |  |  | 417 |  |  | 73 |  |  |  |  |  | 6 |  |  |  | 630 |  | 700 |  |  |  | 610 |  |  | 450 |  |  | 450 |  |  | 400 |  |  |  | 355 |  |  |  | 50 |  | 40 |  | 4-φ40 |  |  |  |  |  | φ28 |  |
| 6 |  | 3731 |  |  |  | 1065 |  |  |  |  | 760 |  |  |  |  | 1087 |  |  |  |  |  | 150 |  |  |  |  | 384 |  | 950 |  |  |  | 417 |  |  | 73 |  |  |  |  |  | 6 |  |  |  | 1000 |  | 700 |  |  |  | 710 |  |  | 450 |  |  | 450 |  |  | 400 |  |  |  | 400 |  |  |  | 50 |  | 40 |  | 4-φ40 |  |  |  |  |  | φ35 |  |
| 7 |  | 3871 |  |  |  | 1205 |  |  |  |  | 900 |  |  |  |  | 1087 |  |  |  |  |  | 150 |  |  |  |  | 384 |  | 1090 |  |  |  | 417 |  |  | 73 |  |  |  |  |  | 6 |  |  |  | 1000 |  | 700 |  |  |  | 710 |  |  | 450 |  |  | 450 |  |  | 400 |  |  |  | 400 |  |  |  | 50 |  | 40 |  | 4-φ40 |  |  |  |  |  | φ35 |  |
| 8 |  | 4011 |  |  |  | 1345 |  |  |  |  | 1040 |  |  |  |  | 1087 |  |  |  |  |  | 150 |  |  |  |  | 384 |  | 1230 |  |  |  | 417 |  |  | 73 |  |  |  |  |  | 6 |  |  |  | 1000 |  | 700 |  |  |  | 710 |  |  | 450 |  |  | 450 |  |  | 400 |  |  |  | 400 |  |  |  | 50 |  | 40 |  | 4-φ40 |  |  |  |  |  | φ35 |  |
| 9 |  | 4151 |  |  |  | 1485 |  |  |  |  | 1180 |  |  |  |  | 1087 |  |  |  |  |  | 150 |  |  |  |  | 384 |  | 1370 |  |  |  | 417 |  |  | 73 |  |  |  |  |  | 6 |  |  |  | 1000 |  | 700 |  |  |  | 710 |  |  | 450 |  |  | 450 |  |  | 400 |  |  |  | 400 |  |  |  | 50 |  | 40 |  | 4-φ40 |  |  |  |  |  | φ35 |  |
| 10 |  | 4291 |  |  |  | 1626 |  |  |  |  | 1320 |  |  |  |  | 1107 |  |  |  |  |  | 150 |  |  |  |  | 384 |  | 1510 |  |  |  | 417 |  |  | 73 |  |  |  |  |  | 6 |  |  |  | 1120 |  | 700 |  |  |  | 800 |  |  | 450 |  |  | 450 |  |  | 400 |  |  |  | 450 |  |  |  | 50 |  | 40 |  | 4-φ40 |  |  |  |  |  | φ35 |  |

| D、DM、DF、DY 450-60型泵外形安装尺寸表(本身底座) Overall installing dimension sheet(without common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | L |  |  | L1 |  |  |  | L2 |  |  |  |  | L3 |  |  |  | L4 |  |  |  | L5 |  |  |  | L6 |  | L7 |  | L8 |  |  | C |  |  | B | B1 |  |  | B2 | B3 | H |  | H1 |  |  | H2 |  | h |  |  | h1 |  | n-φd |  |  | 4-φk |
| 3 |  | 3281 |  |  | 725 |  |  |  | 390 |  |  |  |  | 1243 |  |  |  | 170 |  |  |  | 537 |  |  |  | 574 |  | 591 |  | 11.5 |  |  | 7 |  |  | 1000 | 850 |  |  | 710 | 500 | 560 |  | 550 |  |  | 400 |  | 45 |  |  | 38 |  | 4-φ42 |  |  | φ35 |
| 4 |  | 3844 |  |  | 860 |  |  |  | 541 |  |  |  |  | 1243 |  |  |  | 160 |  |  |  | 537 |  |  |  | 727 |  | 591 |  | 11.5 |  |  | 7 |  |  | 1000 | 850 |  |  | 710 | 500 | 560 |  | 550 |  |  | 400 |  | 45 |  |  | 38 |  | 4-φ42 |  |  | φ35 |
| 5 |  | 4197 |  |  | 1070 |  |  |  | 694 |  |  |  |  | 1263 |  |  |  | 190 |  |  |  | 537 |  |  |  | 880 |  | 591 |  | 11.5 |  |  | 7 |  |  | 1120 | 850 |  |  | 800 | 500 | 560 |  | 550 |  |  | 450 |  | 45 |  |  | 38 |  | 4-φ42 |  |  | φ35 |
| 6 |  | 4350 |  |  | 1230 |  |  |  | 847 |  |  |  |  | 1263 |  |  |  | 190 |  |  |  | 537 |  |  |  | 1033 |  | 591 |  | 11.5 |  |  | 7 |  |  | 1120 | 850 |  |  | 800 | 500 | 560 |  | 550 |  |  | 450 |  | 45 |  |  | 38 |  | 4-φ42 |  |  | φ35 |
| 7 |  | 4503 |  |  | 1380 |  |  |  | 1000 |  |  |  |  | 1263 |  |  |  | 190 |  |  |  | 537 |  |  |  | 1186 |  | 591 |  | 11.5 |  |  | 7 |  |  | 1120 | 850 |  |  | 800 | 500 | 560 |  | 550 |  |  | 450 |  | 45 |  |  | 38 |  | 4-φ42 |  |  | φ35 |
| 8 |  | 4656 |  |  | 1535 |  |  |  | 1153 |  |  |  |  | 1263 |  |  |  | 190 |  |  |  | 537 |  |  |  | 1339 |  | 591 |  | 11.5 |  |  | 7 |  |  | 1120 | 850 |  |  | 800 | 500 | 560 |  | 550 |  |  | 450 |  | 45 |  |  | 38 |  | 4-φ42 |  |  | φ35 |
| 9 |  | 5179 |  |  | 1685 |  |  |  | 1306 |  |  |  |  | 1423 |  |  |  | 190 |  |  |  | 537 |  |  |  | 1492 |  | 591 |  | 11.5 |  |  | 7 |  |  | 1250 | 850 |  |  | 900 | 500 | 560 |  | 550 |  |  | 500 |  | 45 |  |  | 38 |  | 4-φ42 |  |  | φ42 |
| 10 |  | 5331 |  |  | 1840 |  |  |  | 1459 |  |  |  |  | 1423 |  |  |  | 190 |  |  |  | 537 |  |  |  | 1645 |  | 591 |  | 11.5 |  |  | 7 |  |  | 1250 | 850 |  |  | 900 | 500 | 560 |  | 550 |  |  | 500 |  | 45 |  |  | 38 |  | 4-φ42 |  |  | φ42 |
| D、DM、DF、DY 450-90型泵外形安装尺寸表(本身底座) Overall installing dimension sheet(without common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | L |  |  | L1 |  |  |  |  | L2 |  |  |  | L3 |  |  |  | L4 |  |  |  | L5 |  |  |  | L6 |  | L7 |  | L8 |  |  | C |  |  | B | B1 |  |  | B2 | B3 | H |  | H1 |  |  | H2 |  | h |  |  | h1 |  | n-φd |  |  | 4-φk |
| 2 |  | 4090 |  |  | 821 |  |  |  |  | 331 |  |  |  | 757 |  |  |  | 340 |  |  |  | 754 |  |  |  | 455 |  | 725 |  | 137 |  |  | 6 |  |  | 900 | 1165 |  |  | 750 | 650 | 705 |  | 650 |  |  | 450 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ35 |
| 3 |  | 4210 |  |  | 991 |  |  |  |  | 501 |  |  |  | 927 |  |  |  | 340 |  |  |  | 754 |  |  |  | 625 |  | 725 |  | 137 |  |  | 6 |  |  | 1120 | 1165 |  |  | 950 | 650 | 705 |  | 650 |  |  | 560 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ42 |
| 4 |  | 4380 |  |  | 1161 |  |  |  |  | 671 |  |  |  | 1097 |  |  |  | 340 |  |  |  | 754 |  |  |  | 795 |  | 725 |  | 137 |  |  | 6 |  |  | 1250 | 1165 |  |  | 1000 | 650 | 705 |  | 650 |  |  | 560 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ42 |
| 5 |  | 5000 |  |  | 1331 |  |  |  |  | 841 |  |  |  | 1267 |  |  |  | 340 |  |  |  | 754 |  |  |  | 965 |  | 725 |  | 137 |  |  | 6 |  |  | 1250 | 1165 |  |  | 950 | 650 | 705 |  | 650 |  |  | 630 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ42 |
| 6 |  | 5170 |  |  | 1501 |  |  |  |  | 1011 |  |  |  | 1437 |  |  |  | 340 |  |  |  | 754 |  |  |  | 1135 |  | 725 |  | 137 |  |  | 6 |  |  | 1400 | 1165 |  |  | 1060 | 650 | 705 |  | 650 |  |  | 630 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ42 |
| 7 |  | 5340 |  |  | 1671 |  |  |  |  | 1153 |  |  |  | 1437 |  |  |  | 368 |  |  |  | 754 |  |  |  | 1305 |  | 725 |  | 165 |  |  | 6 |  |  | 1400 | 1165 |  |  | 1060 | 650 | 705 |  | 650 |  |  | 630 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ42 |
| 8 |  | 5380 |  |  | 1841 |  |  |  |  | 1295 |  |  |  | 1437 |  |  |  | 396 |  |  |  | 754 |  |  |  | 1475 |  | 725 |  | 193 |  |  | 6 |  |  | 1400 | 1165 |  |  | 1060 | 650 | 705 |  | 650 |  |  | 710 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ48 |
| 9 |  | 5550 |  |  | 2011 |  |  |  |  | 1437 |  |  |  | 1437 |  |  |  | 424 |  |  |  | 754 |  |  |  | 1645 |  | 725 |  | 221 |  |  | 6 |  |  | 1400 | 1165 |  |  | 1120 | 650 | 705 |  | 650 |  |  | 710 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ48 |
| 10 |  | 5950 |  |  | 2181 |  |  |  |  | 1579 |  |  |  | 1470 |  |  |  | 452 |  |  |  | 754 |  |  |  | 1815 |  | 725 |  | 249 |  |  | 6 |  |  | 1400 | 1165 |  |  | 1120 | 650 | 705 |  | 650 |  |  | 710 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ48 |
| 11 |  | 6120 |  |  | 2351 |  |  |  |  | 1749 |  |  |  | 1030 |  |  |  | 452 |  |  |  | 754 |  |  |  | 1985 |  | 725 |  | 249 |  |  | 6 |  |  | 1400 | 1165 |  |  | 1120 | 650 | 705 |  | 650 |  |  | 710 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ48 |
| 12 |  | 6190 |  |  | 2521 |  |  |  |  | 1919 |  |  |  | 1030 |  |  |  | 452 |  |  |  | 754 |  |  |  | 2155 |  | 725 |  | 249 |  |  | 6 |  |  | 1600 | 1165 |  |  | 1250 | 650 | 705 |  | 650 |  |  | 800 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ48 |
| D、DM、DF、DY 550-50型泵外形安装尺寸表(本身底座) Overall installing dimension sheet(without common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | L |  |  | L1 |  |  |  | L2 |  |  |  |  | L3 |  |  |  | L4 |  |  |  | L5 |  |  |  | L6 |  | L7 |  | L8 |  |  | C |  |  | B | B1 |  |  | B2 | B3 | H |  | H1 |  |  | H2 |  | h |  |  | h1 |  | n-φd |  |  | 4-φk |
| 2 |  | 3448 |  |  | 725 |  |  |  | 390 |  |  |  |  | 1146.5 |  |  |  | 170 |  |  |  | 537 |  |  |  | 421 |  | 591 |  | 11.5 |  |  | 7 |  |  | 900 | 850 |  |  | 630 | 500 | 560 |  | 550 |  |  | 355 |  | 45 |  |  | 40 |  | 4-φ42 |  |  | φ28 |
| 3 |  | 3693 |  |  | 860 |  |  |  | 541 |  |  |  |  | 1166.5 |  |  |  | 160 |  |  |  | 537 |  |  |  | 574 |  | 591 |  | 11.5 |  |  | 7 |  |  | 1000 | 850 |  |  | 710 | 500 | 560 |  | 550 |  |  | 400 |  | 45 |  |  | 40 |  | 4-φ42 |  |  | φ35 |
| 4 |  | 3846 |  |  | 1075 |  |  |  | 694 |  |  |  |  | 1166.5 |  |  |  | 190 |  |  |  | 537 |  |  |  | 727 |  | 591 |  | 11.5 |  |  | 7 |  |  | 1000 | 850 |  |  | 710 | 500 | 560 |  | 550 |  |  | 400 |  | 45 |  |  | 40 |  | 4-φ42 |  |  | φ35 |
| 5 |  | 3999 |  |  | 1230 |  |  |  | 847 |  |  |  |  | 1166.5 |  |  |  | 190 |  |  |  | 537 |  |  |  | 880 |  | 591 |  | 11.5 |  |  | 7 |  |  | 1000 | 850 |  |  | 710 | 500 | 560 |  | 550 |  |  | 400 |  | 45 |  |  | 40 |  | 4-φ42 |  |  | φ35 |
| 6 |  | 4352 |  |  | 1380 |  |  |  | 1000 |  |  |  |  | 1186.5 |  |  |  | 190 |  |  |  | 537 |  |  |  | 1033 |  | 591 |  | 11.5 |  |  | 7 |  |  | 1120 | 850 |  |  | 800 | 500 | 560 |  | 550 |  |  | 450 |  | 45 |  |  | 40 |  | 4-φ42 |  |  | φ35 |
| 7 |  | 4505 |  |  | 1535 |  |  |  | 1153 |  |  |  |  | 1186.5 |  |  |  | 190 |  |  |  | 537 |  |  |  | 1186 |  | 591 |  | 11.5 |  |  | 7 |  |  | 1120 | 850 |  |  | 800 | 500 | 560 |  | 550 |  |  | 450 |  | 45 |  |  | 40 |  | 4-φ42 |  |  | φ35 |
| 8 |  | 4658 |  |  | 1685 |  |  |  | 1306 |  |  |  |  | 1186.5 |  |  |  | 190 |  |  |  | 537 |  |  |  | 1339 |  | 591 |  | 11.5 |  |  | 7 |  |  | 1120 | 850 |  |  | 800 | 500 | 560 |  | 550 |  |  | 450 |  | 45 |  |  | 40 |  | 4-φ42 |  |  | φ35 |
| 9 |  | 5181 |  |  | 1840 |  |  |  | 1459 |  |  |  |  | 1346.5 |  |  |  | 190 |  |  |  | 537 |  |  |  | 1492 |  | 591 |  | 11.5 |  |  | 7 |  |  | 1250 | 850 |  |  | 900 | 500 | 560 |  | 550 |  |  | 500 |  | 45 |  |  | 40 |  | 4-φ42 |  |  | φ42 |
| D、DM、DF、DY 650-70型泵外形安装尺寸表(本身底座) Overall installing dimension sheet(without common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | L |  |  | L1 |  |  |  | L2 |  |  |  |  | L3 |  |  |  | L4 |  |  |  | L5 |  |  |  | L6 |  | L7 |  | L8 |  |  | C |  |  | B |  | B1 |  |  | B2 | B3 | H |  | H1 |  |  | H2 |  | h |  |  | h1 |  | n-φd |  |  | 4-φk |
| 2 | 3691 |  |  | 697 |  |  |  | 317 |  |  |  |  | 1363 |  |  |  | 190 |  |  |  | 465 |  |  |  | 599 |  | 638 |  | 111 |  |  | 7 |  |  | 1000 |  | 950 |  |  | 710 | 615 | 620 |  | 540 |  |  | 400 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ35 |
| 3 | 3869 |  |  | 875 |  |  |  | 495 |  |  |  |  | 1363 |  |  |  | 190 |  |  |  | 465 |  |  |  | 777 |  | 638 |  | 111 |  |  | 7 |  |  | 1000 |  | 950 |  |  | 710 | 615 | 620 |  | 540 |  |  | 400 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ35 |
| 4 | 4236 |  |  | 1053 |  |  |  | 673 |  |  |  |  | 1383 |  |  |  | 190 |  |  |  | 465 |  |  |  | 955 |  | 638 |  | 111 |  |  | 7 |  |  | 1120 |  | 950 |  |  | 800 | 615 | 620 |  | 540 |  |  | 450 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ35 |
| 5 | 4414 |  |  | 1231 |  |  |  | 851 |  |  |  |  | 1383 |  |  |  | 190 |  |  |  | 465 |  |  |  | 1133 |  | 638 |  | 111 |  |  | 7 |  |  | 1120 |  | 950 |  |  | 800 | 615 | 620 |  | 540 |  |  | 450 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ35 |
| 6 | 4795 |  |  | 1409 |  |  |  | 1029 |  |  |  |  | 1543 |  |  |  | 190 |  |  |  | 465 |  |  |  | 1311 |  | 638 |  | 111 |  |  | 7 |  |  | 1250 |  | 950 |  |  | 900 | 615 | 620 |  | 540 |  |  | 500 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ42 |
| 7 | 4973 |  |  | 1587 |  |  |  | 1207 |  |  |  |  | 1543 |  |  |  | 190 |  |  |  | 465 |  |  |  | 1489 |  | 638 |  | 111 |  |  | 7 |  |  | 1250 |  | 950 |  |  | 900 | 615 | 620 |  | 540 |  |  | 500 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ42 |
| 8 | 5679 |  |  | 1765 |  |  |  | 1385 |  |  |  |  | 1568 |  |  |  | 190 |  |  |  | 465 |  |  |  | 1677 |  | 638 |  | 111 |  |  | 7 |  |  | 1400 |  | 950 |  |  | 1000 | 615 | 620 |  | 540 |  |  | 560 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ42 |
| D、DM、DF、DY 740-80型泵外形安装尺寸表(本身底座) Overall installing dimension sheet(without common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | L |  |  | L1 |  |  |  | L2 |  |  |  |  | L3 |  |  |  | L4 |  |  |  | L5 |  |  |  | L6 |  | L7 |  | L8 |  |  | C |  |  | B |  | B1 |  | B2 |  | B3 | H |  | H1 |  |  | H2 |  | h |  |  | h1 |  | n-φd |  |  | 4-φk |
| 2 | 3680 |  |  | 697 |  |  |  | 317 |  |  |  |  | 1363 |  |  |  | 190 |  |  |  | 465 |  |  |  | 599 |  | 638 |  | 111 |  |  | 7 |  |  | 1000 |  | 950 |  | 710 |  | 615 | 620 |  | 540 |  |  | 400 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ35 |
| 3 | 4069 |  |  | 875 |  |  |  | 495 |  |  |  |  | 1383 |  |  |  | 190 |  |  |  | 465 |  |  |  | 777 |  | 638 |  | 111 |  |  | 7 |  |  | 1120 |  | 950 |  | 800 |  | 615 | 620 |  | 540 |  |  | 450 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ35 |
| 4 | 4615 |  |  | 1053 |  |  |  | 673 |  |  |  |  | 1543 |  |  |  | 190 |  |  |  | 465 |  |  |  | 955 |  | 638 |  | 111 |  |  | 7 |  |  | 1250 |  | 950 |  | 900 |  | 615 | 620 |  | 540 |  |  | 500 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ42 |
| 5 | 4793 |  |  | 1231 |  |  |  | 851 |  |  |  |  | 1543 |  |  |  | 190 |  |  |  | 465 |  |  |  | 1133 |  | 638 |  | 111 |  |  | 7 |  |  | 1250 |  | 950 |  | 900 |  | 615 | 620 |  | 540 |  |  | 500 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ42 |
| 6 | 5321 |  |  | 1409 |  |  |  | 1029 |  |  |  |  | 1568 |  |  |  | 190 |  |  |  | 465 |  |  |  | 1311 |  | 638 |  | 111 |  |  | 7 |  |  | 1400 |  | 950 |  | 1000 |  | 615 | 620 |  | 540 |  |  | 560 |  | 50 |  |  | 40 |  | 4-φ42 |  |  | φ42 |
| 80D、DM、DF、DY12型泵外形安装尺寸表(共用底座) Overall installing dimension sheet(with common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | L |  |  |  | L1 |  |  |  |  | L2 |  |  |  | L3 |  |  |  | L4 |  |  |  | L5 |  |  |  | L6 |  |  | L7 |  |  | L8 |  |  | C | B1 |  |  | B2 |  | B3 |  |  | H |  | H1 |  | H2 |  |  |  | h |  | n-φd |  |
| 2 |  |  | 1153 |  |  |  | 1120 |  |  |  |  | - |  |  |  | 785 |  |  |  | 180 |  |  |  | 255 |  |  |  | 195 |  |  | 290 |  |  | -40 |  |  | 3 | 410 |  |  | 410 |  | 170 |  |  | 260 |  | 210 |  | 112 |  |  |  | 35 |  | 4-φ24 |  |
| 3 |  |  | 1298 |  |  |  | 1120 |  |  |  |  | - |  |  |  | 785 |  |  |  | 180 |  |  |  | 255 |  |  |  | 265 |  |  | 290 |  |  | 20 |  |  | 3 | 410 |  |  | 410 |  | 170 |  |  | 260 |  | 210 |  | 132 |  |  |  | 35 |  | 4-φ24 |  |
| 4 |  |  | 1368 |  |  |  | 1120 |  |  |  |  | - |  |  |  | 785 |  |  |  | 180 |  |  |  | 255 |  |  |  | 335 |  |  | 290 |  |  | 80 |  |  | 3 | 410 |  |  | 410 |  | 170 |  |  | 260 |  | 210 |  | 132 |  |  |  | 35 |  | 4-φ24 |  |
| 5 |  |  | 1574 |  |  |  | 1400 |  |  |  |  | - |  |  |  | 1060 |  |  |  | 165 |  |  |  | 255 |  |  |  | 405 |  |  | 293 |  |  | -15 |  |  | 3 | 430 |  |  | 430 |  | 170 |  |  | 280 |  | 210 |  | 160 |  |  |  | 40 |  | 4-φ24 |  |
| 6 |  |  | 1644 |  |  |  | 1400 |  |  |  |  | - |  |  |  | 1060 |  |  |  | 165 |  |  |  | 255 |  |  |  | 475 |  |  | 293 |  |  | 55 |  |  | 3 | 430 |  |  | 430 |  | 170 |  |  | 280 |  | 210 |  | 160 |  |  |  | 40 |  | 4-φ24 |  |
| 7 |  |  | 1714 |  |  |  | 1580 |  |  |  |  | - |  |  |  | 1065 |  |  |  | 345 |  |  |  | 255 |  |  |  | 545 |  |  | 293 |  |  | 140 |  |  | 3 | 430 |  |  | 430 |  | 170 |  |  | 270 |  | 210 |  | 160 |  |  |  | 45 |  | 4-φ24 |  |
| 8 |  |  | 1784 |  |  |  | 1580 |  |  |  |  | - |  |  |  | 1065 |  |  |  | 345 |  |  |  | 255 |  |  |  | 615 |  |  | 293 |  |  | 210 |  |  | 3 | 430 |  |  | 430 |  | 170 |  |  | 270 |  | 210 |  | 160 |  |  |  | 45 |  | 4-φ24 |  |
| 9 |  |  | 1899 |  |  |  | 1580 |  |  |  |  | - |  |  |  | 1065 |  |  |  | 345 |  |  |  | 255 |  |  |  | 685 |  |  | 293 |  |  | 270 |  |  | 3 | 430 |  |  | 430 |  | 170 |  |  | 270 |  | 210 |  | 160 |  |  |  | 45 |  | 4-φ24 |  |
| 80 D、DM、DF、DY 30型泵外形安装尺寸表(共用底座) Overall installing dimension sheet(with common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | L |  |  | L1 |  |  |  |  | L2 |  |  |  | L3 |  |  |  | L4 |  |  |  | L5 |  |  |  |  | L6 |  |  | L7 |  |  | L8 |  |  | C | B1 |  |  | B2 |  | B3 |  | H |  |  | H1 |  |  | H2 |  | h |  | n-φd |  |  |
| 3 |  |  | 1449 |  |  | 1140 |  |  |  |  | - |  |  |  | 785 |  |  |  | 200 |  |  |  | 245 |  |  |  |  | 229 |  |  | 300 |  |  | 120 |  |  | 2 | 440 |  |  | 440 |  | 200 |  | 280 |  |  | 205 |  |  | 160 |  | 30 |  | 4-φ24 |  |  |
| 4 |  |  | 1530 |  |  | 1200 |  |  |  |  | - |  |  |  | 785 |  |  |  | 215 |  |  |  | 245 |  |  |  |  | 290 |  |  | 300 |  |  | 140 |  |  | 2 | 440 |  |  | 440 |  | 200 |  | 275 |  |  | 205 |  |  | 180 |  | 30 |  | 4-φ24 |  |  |
| 5 |  |  | 1698 |  |  | 1415 |  |  |  |  | - |  |  |  | 1010 |  |  |  | 195 |  |  |  | 245 |  |  |  |  | 351 |  |  | 300 |  |  | 50 |  |  | 2 | 430 |  |  | 490 |  | 200 |  | 300 |  |  | 205 |  |  | 200 |  | 40 |  | 4-φ24 |  |  |
| 6 |  |  | 1759 |  |  | 1415 |  |  |  |  | - |  |  |  | 1010 |  |  |  | 195 |  |  |  | 245 |  |  |  |  | 412 |  |  | 300 |  |  | 110 |  |  | 2 | 430 |  |  | 490 |  | 200 |  | 300 |  |  | 205 |  |  | 200 |  | 40 |  | 4-φ24 |  |  |
| 7 |  |  | 1860 |  |  | 1520 |  |  |  |  | - |  |  |  | 995 |  |  |  | 265 |  |  |  | 245 |  |  |  |  | 473 |  |  | 300 |  |  | 165 |  |  | 2 | 440 |  |  | 540 |  | 200 |  | 335 |  |  | 205 |  |  | 225 |  | 45 |  | 4-φ24 |  |  |
| 8 |  |  | 2036 |  |  | 1820 |  |  |  |  | 665 |  |  |  | 1330 |  |  |  | 240 |  |  |  | 245 |  |  |  |  | 534 |  |  | 300 |  |  | 60 |  |  | 2 | 455 |  |  | 600 |  | 200 |  | 350 |  |  | 205 |  |  | 250 |  | 40 |  | 6-φ24 |  |  |
| 9 |  |  | 2097 |  |  | 1820 |  |  |  |  | 665 |  |  |  | 1330 |  |  |  | 240 |  |  |  | 245 |  |  |  |  | 595 |  |  | 300 |  |  | 90 |  |  | 2 | 455 |  |  | 600 |  | 200 |  | 350 |  |  | 205 |  |  | 250 |  | 40 |  | 6-φ24 |  |  |
| 10 |  |  | 2158 |  |  | 1820 |  |  |  |  | 665 |  |  |  | 1330 |  |  |  | 240 |  |  |  | 245 |  |  |  |  | 656 |  |  | 300 |  |  | 150 |  |  | 2 | 455 |  |  | 600 |  | 200 |  | 350 |  |  | 205 |  |  | 250 |  | 40 |  | 6-φ24 |  |  |

| 100 D、DM、DF、DY 16型泵外形安装尺寸表(共用底座) Overall installing dimension sheet(with common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | L |  | L1 |  |  | L2 |  |  | L3 |  |  | L4 |  |  | L5 |  |  | L6 |  |  | L7 |  |  |  | L8 |  |  | C |  | B1 |  |  | B2 |  |  | B3 |  |  | H |  |  | H1 |  |  | H2 |  |  | h |  | n-φd |  |  |
| 2 |  | 1260 |  | 1010 |  |  | - |  |  | 635 |  |  | 190 |  |  | 275 |  |  | 229 |  |  | 266 |  |  |  | 135 |  |  | 2 |  | 500 |  |  | 500 |  |  | 220 |  |  | 250 |  |  | 230 |  |  | 132 |  |  | 40 |  | 4-φ27 |  |  |
| 3 |  | 1470 |  | 1260 |  |  | - |  |  | 850 |  |  | 190 |  |  | 275 |  |  | 306 |  |  | 266 |  |  |  | 35 |  |  | 2 |  | 480 |  |  | 480 |  |  | 220 |  |  | 285 |  |  | 230 |  |  | 160 |  |  | 40 |  | 4-φ25 |  |  |
| 4 |  | 1589 |  | 1260 |  |  | - |  |  | 850 |  |  | 190 |  |  | 275 |  |  | 383 |  |  | 266 |  |  |  | 110 |  |  | 2 |  | 480 |  |  | 480 |  |  | 220 |  |  | 285 |  |  | 230 |  |  | 160 |  |  | 40 |  | 4-φ25 |  |  |
| 5 |  | 1696 |  | 1415 |  |  | - |  |  | 1020 |  |  | 205 |  |  | 275 |  |  | 460 |  |  | 276 |  |  |  | 50 |  |  | 2 |  | 450 |  |  | 450 |  |  | 220 |  |  | 295 |  |  | 230 |  |  | 180 |  |  | 40 |  | 4-φ23 |  |  |
| 6 |  | 1773 |  | 1415 |  |  | - |  |  | 1020 |  |  | 205 |  |  | 275 |  |  | 537 |  |  | 276 |  |  |  | -45 |  |  | 2 |  | 450 |  |  | 450 |  |  | 220 |  |  | 325 |  |  | 230 |  |  | 180 |  |  | 40 |  | 4-φ23 |  |  |
| 7 |  | 1967 |  | 1820 |  |  | - |  |  | 1000 |  |  | 410 |  |  | 275 |  |  | 614 |  |  | 288 |  |  |  | 225 |  |  | 2 |  | 545 |  |  | 545 |  |  | 220 |  |  | 300 |  |  | 230 |  |  | 200 |  |  | 40 |  | 4-φ26 |  |  |
| 8 |  | 2046 |  | 1820 |  |  | - |  |  | 1000 |  |  | 410 |  |  | 275 |  |  | 691 |  |  | 288 |  |  |  | 275 |  |  | 2 |  | 545 |  |  | 545 |  |  | 220 |  |  | 300 |  |  | 230 |  |  | 200 |  |  | 40 |  | 4-φ26 |  |  |
| 9 |  | 2123 |  | 1820 |  |  | - |  |  | 1000 |  |  | 410 |  |  | 275 |  |  | 768 |  |  | 288 |  |  |  | 315 |  |  | 2 |  | 545 |  |  | 545 |  |  | 220 |  |  | 300 |  |  | 230 |  |  | 200 |  |  | 40 |  | 4-φ26 |  |  |
| 100 D、DM、DF、DY 45型泵外形安装尺寸表(共用底座) Overall installing dimension sheet(with common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | L |  |  | L1 |  |  | L2 |  |  | L3 |  |  | L4 |  |  | L5 |  |  | L6 |  |  | L7 |  |  |  | L8 |  |  | C |  | B1 |  |  | B2 |  | B3 |  |  | H |  |  |  | H1 |  | H2 |  |  | h |  |  | n-φd |  |
| 2 |  | 1641 |  |  | 1250 |  |  | - |  |  | 840 |  |  | 200 |  |  | 304 |  |  | 203 |  |  | 340 |  |  |  | 110 |  |  | 4 |  | 520 |  |  | 520 |  | 250 |  |  | 325 |  |  |  | 250 |  | 200 |  |  | 30 |  |  | 4-φ24 |  |
| 3 |  | 1870 |  |  | 1520 |  |  | - |  |  | 1040 |  |  | 230 |  |  | 304 |  |  | 277 |  |  | 340 |  |  |  | 130 |  |  | 4 |  | 530 |  |  | 635 |  | 250 |  |  | 360 |  |  |  | 250 |  | 250 |  |  | 40 |  |  | 4-φ24 |  |
| 4 |  | 2014 |  |  | 1690 |  |  | 560 |  |  | 1120 |  |  | 310 |  |  | 304 |  |  | 351 |  |  | 340 |  |  |  | 145 |  |  | 4 |  | 520 |  |  | 670 |  | 250 |  |  | 385 |  |  |  | 250 |  | 280 |  |  | 35 |  |  | 6-φ24 |  |
| 5 |  | 2137 |  |  | 1690 |  |  | 560 |  |  | 1120 |  |  | 310 |  |  | 304 |  |  | 425 |  |  | 340 |  |  |  | 205 |  |  | 4 |  | 520 |  |  | 670 |  | 250 |  |  | 385 |  |  |  | 250 |  | 280 |  |  | 35 |  |  | 6-φ24 |  |
| 本身底座 Without common base |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | L |  | L1 |  |  | L2 |  |  | L3 |  |  | L4 |  |  | L5 |  |  | L6 |  |  | L7 |  |  | L8 | C |  |  | B |  |  |  | B1 | B2 |  |  | B3 |  |  | H |  |  | H1 |  |  | H2 |  |  | h |  | n-φd |  |  | 4-φk |
| 4 | 2014 |  | 600 |  |  | 330 |  |  | 707 |  |  | 135 |  |  | 304 |  |  | 351 |  |  | 340 |  |  | 3 | 4 |  |  | 368 |  |  |  | 520 | 460 |  |  | 250 |  |  | 345 |  |  | 250 |  |  | 280 |  |  | 40 |  | 4-φ24 |  |  | φ24 |
| 5 | 2137 |  | 750 |  |  | 380 |  |  | 694 |  |  | 190 |  |  | 304 |  |  | 425 |  |  | 340 |  |  | 40 | 4 |  |  | 419 |  |  |  | 540 | 535 |  |  | 250 |  |  | 345 |  |  | 250 |  |  | 280 |  |  | 40 |  | 4-φ24 |  |  | φ24 |
| 6 | 2408 |  | 750 |  |  | 380 |  |  | 785 |  |  | 190 |  |  | 304 |  |  | 499 |  |  | 340 |  |  | 53 | 4 |  |  | 406 |  |  |  | 540 | 535 |  |  | 250 |  |  | 345 |  |  | 250 |  |  | 315 |  |  | 40 |  | 4-φ24 |  |  | φ28 |
| 7 | 2552 |  | 750 |  |  | 380 |  |  | 821 |  |  | 190 |  |  | 304 |  |  | 573 |  |  | 340 |  |  | 90 | 4 |  |  | 457 |  |  |  | 540 | 535 |  |  | 250 |  |  | 345 |  |  | 250 |  |  | 315 |  |  | 40 |  | 4-φ24 |  |  | φ28 |
| 8 | 2626 |  | 900 |  |  | 525 |  |  | 779 |  |  | 190 |  |  | 304 |  |  | 647 |  |  | 340 |  |  | 61 | 4 |  |  | 457 |  |  |  | 520 | 510 |  |  | 250 |  |  | 345 |  |  | 250 |  |  | 315 |  |  | 40 |  | 4-φ26 |  |  | φ28 |
| 9 | 2700 |  | 900 |  |  | 525 |  |  | 816 |  |  | 190 |  |  | 304 |  |  | 721 |  |  | 340 |  |  | 98 | 4 |  |  | 457 |  |  |  | 520 | 510 |  |  | 250 |  |  | 345 |  |  | 250 |  |  | 315 |  |  | 40 |  | 4-φ26 |  |  | φ28 |
| 125 D、DM、DF、DY 25型泵外形安装尺寸表(共用底座) Overall installing dimension sheet(with common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | L |  |  | L1 |  |  | L2 |  |  | L3 |  |  | L4 |  |  | L5 |  |  | L6 |  |  | L7 |  |  |  | L8 |  |  | C |  | B1 |  |  | B2 |  |  | B3 |  |  | H |  |  | H1 |  |  | H2 |  |  | h |  | n-φd |  |
| 2 |  | 1477 |  |  | 1180 |  |  | - |  |  | 740 |  |  | 210 |  |  | 245 |  |  | 262 |  |  | 287 |  |  |  | 125 |  |  | 2 |  | 520 |  |  | 520 |  |  | 280 |  |  | 335 |  |  | 300 |  |  | 180 |  |  | 40 |  | 4-φ24 |  |
| 3 |  | 1676 |  |  | 1480 |  |  | - |  |  | 1010 |  |  | 250 |  |  | 245 |  |  | 352 |  |  | 287 |  |  |  | 45 |  |  | 2 |  | 555 |  |  | 555 |  |  | 280 |  |  | 315 |  |  | 300 |  |  | 200 |  |  | 40 |  | 4-φ24 |  |
| 4 |  | 1766 |  |  | 1480 |  |  | - |  |  | 1010 |  |  | 250 |  |  | 245 |  |  | 442 |  |  | 287 |  |  |  | 135 |  |  | 2 |  | 555 |  |  | 555 |  |  | 280 |  |  | 315 |  |  | 300 |  |  | 200 |  |  | 40 |  | 4-φ24 |  |
| 5 |  | 1906 |  |  | 1560 |  |  | 530 |  |  | 1060 |  |  | 235 |  |  | 245 |  |  | 532 |  |  | 297 |  |  |  | 115 |  |  | 2 |  | 560 |  |  | 560 |  |  | 280 |  |  | 365 |  |  | 300 |  |  | 225 |  |  | 40 |  | 6-φ24 |  |
| 6 |  | 2111 |  |  | 1740 |  |  | 555 |  |  | 1115 |  |  | 360 |  |  | 245 |  |  | 622 |  |  | 297 |  |  |  | 275 |  |  | 2 |  | 530 |  |  | 600 |  |  | 280 |  |  | 350 |  |  | 300 |  |  | 250 |  |  | 40 |  | 6-φ24 |  |
| 7 |  | 2271 |  |  | 2210 |  |  | 700 |  |  | 1410 |  |  | 380 |  |  | 245 |  |  | 712 |  |  | 297 |  |  |  | 160 |  |  | 2 |  | 610 |  |  | 705 |  |  | 280 |  |  | 395 |  |  | 300 |  |  | 280 |  |  | 60 |  | 6-φ24 |  |
| 8 |  | 2361 |  |  | 2210 |  |  | 700 |  |  | 1410 |  |  | 380 |  |  | 245 |  |  | 802 |  |  | 297 |  |  |  | 215 |  |  | 2 |  | 610 |  |  | 705 |  |  | 280 |  |  | 395 |  |  | 300 |  |  | 280 |  |  | 60 |  | 6-φ24 |  |
| 9 |  | 2501 |  |  | 2210 |  |  | 700 |  |  | 1410 |  |  | 380 |  |  | 245 |  |  | 892 |  |  | 297 |  |  |  | 295 |  |  | 4 |  | 610 |  |  | 705 |  |  | 280 |  |  | 395 |  |  | 300 |  |  | 280 |  |  | 60 |  | 6-φ24 |  |

| 150 D、DM、DF、DY 30型泵外形安装尺寸表(共用底座) Overall installing dimension sheet(with common base) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | L |  | L1 |  | L2 | L3 |  | L4 |  | L5 |  | L6 |  | L7 |  | L8 |  | C |  | B1 |  |  | B2 |  | B3 |  | H | H1 |  | H2 |  | h | n-φd |  |
| 2 |  | 1916 |  | 1980 |  | 680 | 1350 |  | 315 |  | 365 |  | 310 |  | 388 |  | -25 |  | 4 |  | 660 |  |  | 660 |  | 350 |  | 400 | 350 |  | 225 |  | 35 | 6-φ26 |  |
| 3 |  | 2186 |  | 1980 |  | 680 | 1350 |  | 315 |  | 365 |  | 425 |  | 388 |  | 90 |  | 4 |  | 660 |  |  | 660 |  | 350 |  | 400 | 350 |  | 280 |  | 35 | 6-φ26 |  |
| 4 |  | 2351 |  | 1980 |  | 680 | 1350 |  | 315 |  | 365 |  | 540 |  | 388 |  | 210 |  | 4 |  | 660 |  |  | 660 |  | 350 |  | 400 | 350 |  | 280 |  | 35 | 6-φ26 |  |
| 5 |  | 2710 |  | 2400 |  | 750 | 1500 |  | 530 |  | 365 |  | 655 |  | 418 |  | 230 |  | 4 |  | 580 |  |  | 720 |  | 350 |  | 445 | 350 |  | 315 |  | 35 | 6-φ26 |  |
| 6 |  | 2897 |  | 2400 |  | 750 | 1500 |  | 530 |  | 365 |  | 770 |  | 418 |  | 345 |  | 4 |  | 580 |  |  | 720 |  | 350 |  | 445 | 350 |  | 315 |  | 35 | 6-φ26 |  |
| 7 |  | 3014 |  | 2400 |  | 750 | 1500 |  | 530 |  | 365 |  | 885 |  | 418 |  | 460 |  | 4 |  | 580 |  |  | 720 |  | 350 |  | 445 | 350 |  | 315 |  | 35 | 6-φ26 |  |
| 本身底座 Without common base |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | L |  | L1 |  | L2 |  | L3 | L4 |  | L5 |  | L6 |  | L7 |  | L8 |  | C |  | B |  | B1 | B2 |  | B3 |  | H | H1 |  | H2 |  | h | n-φd |  | 4-φk |
| 2 | 1916 |  | 740 |  | 450 |  | 605 | 140 |  | 365 |  | 310 |  | 388 |  | -70 |  | 4 |  | 311 |  | 600 | 356 |  | 350 |  | 400 | 350 |  | 225 |  | 50 | 4-φ26 |  | φ24 |
| 3 | 2186 |  | 740 |  | 450 |  | 746 | 140 |  | 365 |  | 425 |  | 388 |  | -12.5 |  | 4 |  | 368 |  | 600 | 457 |  | 350 |  | 400 | 350 |  | 280 |  | 50 | 4-φ26 |  | φ24 |
| 4 | 2351 |  | 740 |  | 450 |  | 804 | 140 |  | 365 |  | 540 |  | 388 |  | 45 |  | 4 |  | 419 |  | 600 | 457 |  | 350 |  | 400 | 350 |  | 280 |  | 50 | 4-φ26 |  | φ24 |
| 5 | 2710 |  | 1060 |  | 805 |  | 811 | 140 |  | 365 |  | 655 |  | 418 |  | 70 |  | 4 |  | 406 |  | 580 | 508 |  | 350 |  | 400 | 350 |  | 315 |  | 40 | 4-φ27 |  | φ28 |
| 6 | 2897 |  | 1060 |  | 805 |  | 868 | 140 |  | 365 |  | 770 |  | 418 |  | 12.5 |  | 4 |  | 457 |  | 580 | 508 |  | 350 |  | 400 | 350 |  | 315 |  | 40 | 4-φ27 |  | φ28 |
| 7 | 3014 |  | 1060 |  | 805 |  | 958 | 140 |  | 365 |  | 885 |  | 418 |  | -45 |  | 4 |  | 457 |  | 580 | 508 |  | 350 |  | 400 | 350 |  | 315 |  | 40 | 4-φ27 |  | φ28 |
| 8 | 3130 |  | 1500 |  | 1210 |  | 821 | 145 |  | 365 |  | 1000 |  | 418 |  | -105 |  | 4 |  | 508 |  | 595 | 508 |  | 350 |  | 400 | 350 |  | 315 |  | 40 | 4-φ25 |  | φ28 |
| 9 | 3245 |  | 1500 |  | 1210 |  | 878 | 145 |  | 365 |  | 1115 |  | 418 |  | -47.5 |  | 5 |  | 508 |  | 595 | 508 |  | 350 |  | 400 | 350 |  | 315 |  | 40 | 4-φ25 |  | φ28 |
| 10 | 3590 |  | 1500 |  | 1210 |  | 903 | 145 |  | 365 |  | 1230 |  | 418 |  | 10 |  | 5 |  | 560 |  | 595 | 610 |  | 350 |  | 400 | 350 |  | 355 |  | 40 | 4-φ25 |  | φ28 |

| 法兰尺寸表 Sheet of Flange dimension |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 泵 型 号 Pump type |  | 进口法兰 Inlet flange |  |  |  |  |  |  |  | 出口法兰 Outlet flange |  |  |  |  |  |  |  |
|  |  | Dg | D | D1 | D2 | D3 | b | f1/f2 | n-φd | Dg | D | D1 | D2 | D3 | b | f1/f2 | n-φd |
| D DF DY DM | 6-25 | 40 | 130 | 100 | 80 |  | 16 | -/3 | 4-13.5 | 40 | 150 | 110 | 88 | 75 | 20 | 4/3 | 4-17.5 |
| D DF DY DM | 6-50 | 50 | 160 | 110 | 90 |  | 30 | -/3 | 4-13.5 | 50 | 175 | 135 | 105 | 87 | 28 | 4/3 | 4-23 |
| D DF DY DM | 12-25 | 50 | 140 | 110 | 90 |  | 16 | -/3 | 4-13.5 | 40 | 150 | 110 | 88 | 75 | 20 | 4/3 | 4-17.5 |
| D DF DY DM | 12-50 | 50 | 160 | 110 | 90 |  | 30 | -/3 | 4-13.5 | 50 | 175 | 135 | 105 | 87 | 28 | 4/3 | 4-23 |
| D DF DY DM | 25-30 | 65 | 160 | 130 | 110 |  | 16 | -/3 | 4-13.5 | 65 | 185 | 145 | 122 | 109 | 24 | 4/3 | 8-17.5 |
| D DY DM | 25-50 | 80 | 190 | 150 | 128 |  | 18 | -/3 | 4-17.5 | 80 | 215 | 170 | 133 | 120 | 30 | 4/3 | 8-22 |
| DF | 25-50 | 80 | 215 | 170 | 133 | 120 | 30 | 4/3 | 8-22 |  |  |  |  |  |  |  |  |
| D DF DY DM | 46-30 | 80 | 190 | 150 | 128 |  | 18 | -/3 | 4-17.5 | 65 | 185 | 145 | 122 | 109 | 24 | 4/3 | 8-17.5 |
| D | 46-50 | 80 | 190 | 150 | 128 |  | 18 | -/3 | 4-17.5 | 80 | 215 | 170 | 133 | 120 | 30 | 4/3 | 8-22 |
| DF DY DM | 46-50 | 80 | 215 | 170 | 133 | 120 | 30 | 4/3 | 8-22 |  |  |  |  |  |  |  |  |
| D DF DY DM | 85-45 | 100 | 210 | 170 | 148 |  | 18 | -/3 | 4-17.5 | 100 | 235 | 190 | 158 | 149 | 28 | 4.5/3 | 8-22 |
| D DY DM | 85-67 | 150 | 265 | 225 | 202 |  | 20 | -/3 | 8-17.5 | 150 | 345 | 280 | 212 | 203 | 33 | 4.5/3 | 8-33 |
| DF | 85-67 | 150 | 345 | 280 | 212 | 203 | 33 | 4.5/3 | 8-33 |  |  |  |  |  |  |  |  |
| D DF DY DM | 120-50 | 125 | 240 | 200 | 178 |  | 20 | -/3 | 8-17.5 | 125 | 270 | 220 | 184 | 175 | 30 | 4.5/3 | 8-26 |
| D DF DY DM | 155-30 | 150 | 285 | 240 | 212 |  | 26 | -/3 | 8-22 | 150 | 300 | 250 | 212 | 203 | 34 | 4.5/3 | 8-26 |
| D DY DM | 155-67 | 150 | 265 | 225 | 202 |  | 20 | -/3 | 8-17.5 | 150 | 345 | 280 | 212 | 203 | 33 | 4.5/3 | 8-33 |
| DF | 155-67 | 150 | 345 | 280 | 212 | 203 | 33 | 4.5/3 | 8-33 |  |  |  |  |  |  |  |  |
| D DF DY DM | 280-43 | 200 | 340 | 295 | 268 |  | 28 | -/3 | 8-22 | 200 | 375 | 320 | 285 | 259 | 38 | 4.5/3 | 12-30 |
| D DF DY DM | 280-65 | 200 | 340 | 295 | 268 |  | 30 | -/3 | 12-22 | 200 | 415 | 345 | 285 | 259 | 44 | 4.5/3 | 12-36 |
| D DF DY DM | 280-80 | 200 | 360 | 310 | 278 |  | 30 | -/3 | 12-26 | 200 | 430 | 360 | 284 | - | 44 | -/3 | 12-41 |
| D DF DY DM | 280-100 | 200 | 360 | 310 | 270 |  | 42 | -/3 | 12-26 | 150 | 350 | 290 | 250 | 203 | 44 | 5/3 | 12-34 |
| D DF DY DM | 360-40 | 200 | 340 | 295 | 268 |  | 28 | -/3 | 8-22 | 200 | 375 | 320 | 285 | 259 | 38 | 4.5/3 | 12-30 |
| D DF DY DM | 450-60 | 250 | 405 | 355 | 320 |  | 32 | -/3 | 12-26 | 250 | 470 | 400 | 345 | 312 | 48 | 4.5/3 | 12-36 |
| D DF DY DM | 450-90 | 250 | 435 | 370 | 332 |  | 41 | -/3 | 12-30 | 250 | 500 | 430 | 382 | 312 | 48 | 4.5/3 | 12-41 |
| D DF DY DM | 550-50 | 250 | 405 | 355 | 320 |  | 32 | -/3 | 12-26 | 250 | 470 | 400 | 345 | 312 | 48 | 4.5/3 | 12-36 |
| D DF DY DM | 650-70 | 300 | 530 | 460 | 412 |  | 32 | -/3 | 16-41 | 300 | 585 | 500 | 442 |  | 48 | 4.5/3 | 16-48 |
| D DF DY DM | 740-80 | 300 | 530 | 460 | 412 |  | 32 | -/3 | 16-41 | 300 | 585 | 500 | 442 |  | 48 | 4.5/3 | 16-48 |
| 80D-12 |  | 80 | 190 | 150 | 128 |  | 18 | -/3 | 4-17.5 | 80 | 200 | 160 | 133 |  | 26 | -/3 | 8-17.5 |
| 80D-30 |  | 80 | 195 | 160 | 135 |  | 22 | -/3 | 4-17.5 | 80 | 200 | 160 | 133 |  | 26 | -/3 | 8-17.5 |
| 100D-16 |  | 100 | 210 | 170 | 148 |  | 18 | -/3 | 4-17.5 | 100 | 220 | 180 | 158 |  | 24 | -/3 | 8-17.5 |
| 100D-45 |  | 100 | 210 | 170 | 148 |  | 18 | -/3 | 4-17.5 | 100 | 235 | 190 | 158 | 149 | 28 | 4.5/3 | 8-22 |
| 125D-25 |  | 125 | 240 | 200 | 178 |  | 20 | -/3 | 8-17.5 | 125 | 270 | 220 | 184 | 175 | 30 | 4.5/3 | 8-26 |
| 150D-30 |  | 150 | 285 | 240 | 212 |  | 26 | -/3 | 8-22 | 150 | 300 | 250 | 212 | 203 | 34 | 4.5/3 | 8-26 |

泵的装配与拆卸

Assembly and Disassembly

一、装配

本型泵装配质量的好坏直接影响泵能否正常运行，并影响泵的使用寿命和性能参数，影响机组的振动和噪音。装配中应注意以下几点：

1、固定部分各零件组合后的同心度靠零件制造精度和装配质量来保证，应保护零件的加工精度和表面粗糙度，不允许磕碰、划伤。做密封剂用的二硫化钼应干净，紧固用的螺钉、螺栓应受力均匀。

2、叶轮出口流道与导叶进口流道的对中性是依各零件的轴向尺寸来保证，流道对中性的好坏直接影响泵的性能，故泵的尺寸不能随意调整。

3、泵装配完毕后，在未装填料前，用手转动泵转子，检查转子在泵壳体中旋转是否灵活，轴向窜动量是否达到规定的要求。

4、上述检查合格后，在泵的两端轴封处加入填料，注意填料环在填料室中的相对位置。

二、拆卸

1、泵的拆卸按装配相反的顺序进行，拆卸时应严格保护泵上各零件的制造精度不受损伤。

2、拆卸穿杠的同时应将各中段用垫垫起，以免各中段止口松动下沉将轴压弯。

Assembly

Assembly quality of the serial pump is effect directly on pump operating, and effect on pump life, performance, vibration, and noise etc. so the following point should be noted.

- The co-axial degree of all stator parts is replied on parts’ manufacturing precision and assembly quality. So we should ensure the manufacturing precision and surface rough grade. Don’t allow collision & laceration, the MoS2 used for seal should be clean. The force of bolts of bots & screws should be well-distributed.

- The centering degree of impeller discharge passage with diffuser suction passage is replied on these part axial dimensions. The flow passage centering degree is effect on pump performance directly. So these part dimensions can’t be changed at will.

- After assembly, (before insert the packing), rotating the pump rotor by hand, ensure the rotor rotating flexibly, axial tolerance value should be satisfied requirement.

- After all these stated are suitable, insert packing in seal chamber. Ensure the packing ring relative position.

Disassembly:

- Disassembly is according the opposite order of assembly. In disassembly the part precision should not be damaged.

- In disassembly pole, the stage casing should be supported by wedges, to prevent the shaft to be bent down by stage casing.

安装

Installing

本型泵安装时除满足一般安装技术要求外，还应注意以下几点：

- 水泵、电机或底座的地脚螺栓一般留预留孔，采用二次灌浆埋设。

- 电机与水泵组合安装时，应将泵联轴器端轴伸向外拉出，再保证泵和电机两联轴器间的轴向间隙值。

- 泵与电机两轴心线应在同一水平直线上。在两联轴器外圆上的不同心度允差0.1mm，端面间隙沿圆周的不均匀度允差0.3mm。

- 泵只能承受自身内力，不能承受任何外力。

In installing besides common installing technical requirement, following points should be cared.

- The foundation bolts of pump set have preparing holes; it will have second pouring concrete to fill in.

- Installing pump and motor, the pump coupling should be pulling out a little, ensure the required clearance between couplings.

- The axial line should be on the same horizontal line, the centering degree tolerance of couplings is ≤0.1mm, the endface clearance tolerance between the coupling should be less then 0.3mm.

- Pump bear only the internal force, don’t allow to bear any external force.

泵的起动、运行、停车

Starting, Running, and Stopping

起动：

- 泵起动前应先盘动转子，检查转子是否灵活。

- 检查电机转向是否与泵的转向一致；冷却润滑水是否接通。

- 关闭泵的出口闸阀、压力表旋塞，用输送的液体或抽真空系统排出吸入管和泵内的空气。

- 检查泵与电机联接螺栓的松紧程度和泵周围的安全情况，使泵处于准备起动状态。

- 起动泵，待泵运行正常后，打开压力表旋塞，慢慢开启泵出口闸阀，直到所需流量和扬程为止，应尽量在规定的流量和扬程范围内工作，以获得最大的节能效果，泵在运行过程中不应超过最大流量点运行。

运行：

- 本型泵靠泵内平衡机构平衡轴向力，平衡装置内有平衡液流出，平衡液体由平衡水管接至吸入段或在平衡室外设计一短管，平衡液体经短管流向泵外，为保证泵正常运行，平衡水管绝对不允许堵塞。

- 本型泵轴承温升不得高于环境温度35℃，轴承的最高温度不应高于75℃。

- 填料室漏水程度以每分钟20～30滴为宜，以保持轴与填料的正常润滑与冷却。机械密封平均泄露量：当机械密封内径≤50mm时为3ml/h，机封内径＞50mm时为5ml/h。

- 泵轴封采用机械密封时，起动前必须灌满水，防止机械密封干运转。

- 转子在运行中存在一定的轴向游动，应保证电机和水泵两联轴器端面间的间隙值。

- 泵在运行期间应定期检查叶轮、密封环、导叶套、平衡盘、轴套的磨损情况，磨损量过大时应及时更换。

- 泵在使用中应根据具体情况，订出详细的操作规程。

停车：

- 停车前应先关闭压力表旋塞，慢慢关闭出口闸阀，待出口阀关闭完毕后再停电机。

- 冬季冷冻季节，如短期停用水泵时，须放掉泵中的存水，以防止泵冻裂。

- 水泵在停用期间，必须每1月左右起动运转一次，时间不少于5分钟，以保证泵的可靠运转。

Starting

  - Before starting, turn the rotor, it should be flexible.

  - Check motor rotating direction; turn on cooling and lubricating water system.

  - Switch off the fate valve in discharge pipe, pressure meter, pour enough water into pump or prime with vacuum pump.

  - Check the screws in pump and motor, ensure the pump safety, the pump is ready to start.

  - Turn on button, till pump run at normal condition, turn on pressure meter, slowly turn on the fate valve, till reach required flow and head. In order to save more energy, the pump operating working point should not be over than max flow point.

Running

- The axial force of pump is balanced by balance unit, the balance liquid flow out from the unit, the liquid flow out pump through a balance pipe or a short pipe outside of balance chamber, to ensure pump run normally, the balance pipe don’t allow to be clogged.

- Bearing temperature rise of the serial pump is not over 35℃ than ambient temperature. The max temperature is not over 75℃.

- The water leaking flow in packing chamber is 20～30 drop/min, to ensure the shaft and packing lubricating and cooling. The water leaking flow in mechanical seal chamber is 3ml/h at mechanical seal internal dia.≤50mm, its water flow is 5ml/h at mechanical seal internal dia.＞50mm.

- Before starting, the mechanical seal must be passed water, to avoid running in dry condition.

- During running, the rotor has some axial movement, to ensure the clearance between couplings.

- During running, impeller, wearing, diffuser sleeve, balance disc and shaft sleeve should be check usually, when these part is worn out, renew it in time.

- Pump should be making detail program according to practical condition.

Stopping

- Before stopping, turn off pressure meter, slowly turn off the fate valve, till the fate valve is turning off entirely. Then stop motor.

- In winter when the pump need stop for long time, the water inside pump must be released to avoid the pump frost crack.

- During stopping, the pump should be start once in a mouth, the running time is not less 5 minutes, to ensure pump reliable.

故障原因及其解决方法

| 故 障 | 原 因 | 解 决 方 案 |
| --- | --- | --- |
| 水泵不出水 | 1、起动前注入泵内的水不够（当使用真空泵时，则抽真空不够）。 2、转向不对。 3、底阀未打开或被堵塞。 4、泵的吸水高度过高。 5、进水管或仪表联接处漏气。 6、填料函部位漏气。 7、叶轮流道被堵塞。 8、泵的转速不够。 | 1、注水至少淹没叶轮，最好充满泵腔（抽真空时同）。 2、更换电机接线。 3、检查底阀，清洗检修或更新。 4、降低泵的安装高度。 5、拧紧或堵塞漏气处。 6、检查轴套及轴套螺母，漏气时应加垫。 7、清洗叶轮。 8、检查电机，检修或更新。 |
| 流量不足或不出水 | 1、水流通道被堵塞。 2、叶轮和密封环之间的间隙泄漏太大。 3、转速未达到规定值。 | 1、依次检查进出水流道是否畅通，排除堵塞物。 2、检修或更换叶轮和密封环。 3、检查电压是否过低，检查电机是否损坏，检修电机和调整电压。 |
| 水泵消耗功率过大，电机电流超过额定值 | 1、填料压得过紧。 2、泵的转子与定子摩擦。 3、流量超过了使用范围。 4、平衡盘与平衡环摩擦。 5、水泵内间隙过大，泵效率降低。 | 1、调松填料。 2、检查转子与定子摩擦部位。 3、在规定范围内使用水泵。 4、检查平衡盘的端面跳动，磨损太大应更换。 5、解体检查，更换已磨损件。 |
| 水泵响声异常和振动 | 1、发生了汽蚀。 2、机件松动或脱落。 3、转子不平衡。 4、轴弯曲。 5、泵轴与电机轴不同心。 6、基础薄弱。 7、轴承磨损。 8、水泵内间隙过大。 | 1、降低水泵安装高度，简化进水管路，减少管路损失。 2、停车检查，紧固零件。 3、转子做平衡试验，车削不平衡重量。 4、调直主轴。 5、调整机组，使之同心。 6、加固基础。 7、更换轴承。 8、解体检查，更换已磨损件。 |
| 轴承过热 | 1、润滑不良。 2、轴弯曲。 3、轴承损坏。 4、泵轴与电机轴不同心。 5、冷却水不足或断水。 | 1、加油（检查油环，使之旋转）。 2、调直主轴。 3、更换轴承。 4、调整机组，使之同心。 5、检查冷却水情况。 |

Troubles & Remedies

| Troubles | Causes | Remedies |
| --- | --- | --- |
| Pump loses prime | 1. The water poured in the pump is not enough. 2. Incorrect rotating direction. 3. The fate valve is not open or it is plugged up. 4. Suction lift too high. 5. Leakage of air found from the suction pipe or instrument joints. 6. Leakage of air from the packing chamber. 7. The impeller flow passage is clogged. 8. Speed is too low. | 1. Pour water into the pump again. 2. Replacing the motor connection. 3. Correct or renew the foot valve. 4. Make the suction head lower. 5. Block the leaking place. 6. Check sleeve and nuts or add gaskets. 7. Clean the impeller. 8. Repair or renew motor. |
| Not enough capacity or no water is pumped | 1. Flow passage is blocked. 2. The leakage is too big between impeller and wearing. 3. The running speed of pump is lower than rated. | 1. Check flow passage, ensure unblocked. 2. Check or replace impeller and wearing. 3. Check the motor & voltage repair motor or adjust voltage. |
| Pump requires excessive power, the current value is over than the rated. | 1. Packing is too tight. 2. Friction between stator and rotor. 3. Flow is too big. 4. Friction between ring and balance disc. 5. Pump chamber clearance is too big, pump efficiency is too low. | 1. Loosen the packing. 2. Clear out mechanic friction. 3. Adjust the range of flow. 4. Check the balance disc renew the damaged parts 5. Disassemble to check, renew the worn parts. |
| Unexpected noises are heard and vibrates heavily | 1. Cavitation in pump. 2. Part become loose or fall off. 3. Impeller is out of balance. 4. The shaft is bent. 5. The shaft is off-centering. 6. Foundation are loosen. 7. Bearing is worn out. 8. The clearance is too big. | 1. Reduce installing height simplify the suction pipe reduce pipe loss. 2. Stop the pump to check, and tighten the parts. 3. Correct impeller static balance. 4. Correct the shaft. 5. Correct the coaxial degree between pump and motor. 6. Reinforce foundation. 7. Renew bearing. 8. Renew the wearable parts. |
| The bearing is overheated | 1. Lubricating is not well. 2. Shaft is bent. 3. Bearing is damaged. 4. The shaft is off-center. 5. Cooling water is not enough or not water. | 1. Add oil (rotating oil ring). 2. Correct the shaft. 3. Renew the bearing. 4. Correct the pump and the motor shaft co-axial degree. 5. Add cooling water flow. |