SA型

单级双吸水平中开式离心泵

Type SA Single-stage Double-suction Horizontal

Split Centrifugal Pump

安装使用说明书

Instruction On Installation And Operation

长沙福斯水泵泵业有限公司

Fuchs Changsha Pump pump industry limited company

一、概述:

SA型泵系单级、双吸水平中开式离心泵，适应于工厂、城市、矿山、电站、农田、水利工程等领域。用输送不含固体颗粒的清水或物理、化学性质类似于水的其它液体，被输送的介质温度为0℃～80℃。允许最大进口压力0.6Mpa。

参数范围： 流量Q   72～10000m3/h      扬程H  9～110m

型号说明：

如：10SA-6A

10——吸入口径被25除（即吸入口径为250mm）

SA——单级双吸水平中开式离心泵

6——比转数被10除化整的约数

A——表示叶轮外径第一次变化，A、B、C……依次类推

二、结构说明

1、SA型泵的吸入口和排出口均铸在泵体上，成水平方向，与轴线垂直。泵体与泵盖水平分开，以便揭盖检查内部零件时，不必拆卸管路及电动机。从转动一端看，泵轴均为逆时针方向旋转。

2、本型泵的主要结构除轴承部件和轴套有几种不同结构外，其他部分大体相同。轴承部分：有的泵用球轴承，用油杯注油润滑或用油环溅油润滑；有的泵用镶有合金轴瓦的套筒轴承，一端加装单列向心球轴承。双吸泵的轴向力基本上是平衡的，部分末平衡的轴向力，由单列向心球轴承承受之。

轴承的结构：有的泵的轴套带有螺纹，兼作螺母以固定叶轮；有的泵每端用两个轴套，其中一个带有螺纹；有的泵除轴套外，另用轴套螺母，以固定轴套和叶轮。

3、本型泵主要零件有：泵体和泵盖、叶轮、轴、密封环、轴套、轴承体、轴承、填料套和填料环等。

除了轴用优质碳素钢，螺栓、螺钉、螺母，键等零件用钢材制成外，泵的其他零件大部分都用铸铁制成。

泵的叶轮、密封环和位于填料部分的轴套，均为易损件，磨损后可用备件更换。

轴承部分如装有油杯，用钙基油润滑，凡用油环溅油润滑的轴承，用2号或3号锭子油润滑。

- General

Type SA pump belongs to single-stage double-suction split centrifugal pump. It transfers clear water or pure liquids physically and chemically similar to clear water.

The parameters of the type pump are as follows:

Head: 9m~110m

Capacity: 72m3/h~10000 m3/h

Liquid temperature: 80oC

This type pump may be used as a dyainage or water supply pump in factories, mines, cities ,generating stations and hydraulic engineerings, and also as a circulating pump in thermal stations or as a drainage and irrigation pump in agriculture.

Type description, for example: 10SA-6A

10----Inlet diameter divided by 25 (i.e the inlet diameter is 250mm)

SA----Single-stage, double-suction centrifugal pump

6----Approximate number obtained from the specific speed divided by 10

A----An additional symbol represents that the working characteristics of the pump are somewhat changed, but the size of other parts are unchanged, after the outside diameter of  the impeller is cut or the speed of the pump is lowered.

- Structure Description

- The inlet opening and outlet opening of type SA pump are all cast horizontally in the pump body are vertical to the pump shaft centerline. The pump body is separated horizontally from the pump cover in order to inspect the inner parts without disconnecting the pipe lines and the motor(or other prime movers

Looking from the motor, the pump runs in anti-clockwise direction.

- The main structure is identical except the bearing and the sleeve.

Constructions of bearing:

Some of the pumps are mounted with ball bearings, lubricated by filling oil the through the oil cups or by spattering oil from the oil rings; and the others are mounted with a babbiting -lined sleeve bearing to every end of each shaft without the coupling half. The axial thrust of a double suction pump is basically balanced, while a smaller amount which has not yet been balanced is supported by a single row radial ball bearing.

Constructions of shaft sleeve:

For some pumps, the sleeve with screw thread serves as the nut to fix the impeller; for some pumps, each end has two sleeves, of which one with the screw thread; for some pumps, the sleeve nut may fix the sleeve and impeller.

- The main parts: casing, casing cover, impeller, shaft, wearing ring, shaft sleeve, bearing box, bearing, packing sleeve, packing ring and so on.

Most of the parts of the pump are made of cast iron, except that shaft is of quality carbon steel and stud, bolt ,nut and key are of steel.

The impeller, the wearing ring and the shaft sleeve placed in the packing are all easily wearing parts, and may be replaced with spare parts when wearing off.

The bearing with the oil cup is lubricated with grease, the other lubricated by spattering oil from an oil ring is greased with spindle oil No.2 or No.3.

4、填料密封由填料套、填料环、填料和填料压盖等组成。填料室铸在泵体和泵盖上。填料的松紧程度必须适当，以液体能一滴滴渗出为宜，太紧则轴套易发热；太松则液体流失多，都会降低泵的效率。

5、轴承的不同结构（见轴承型号及规格表）

轴承型号及规格表

| 泵 型 号 | 装配 部位 | 轴 承 名 称 | 轴承规格 | 数 量 | 轴承体结构型式 |
| --- | --- | --- | --- | --- | --- |
| 6SA-6 | 从动端 | 深沟球轴承 | 310 | 1 | 结构一 |
|  | 驱动端 | 深沟球轴承 | 310 | 1 |  |
| 6SA-8 | 从动端 | 深沟球轴承 | 308 | 1 |  |
|  | 驱动端 | 深沟球轴承 | 308 | 1 |  |
| 8SA-7 | 从动端 | 深沟球轴承 | 309 | 1 |  |
|  | 驱动端 | 深沟球轴承 | 309 | 1 |  |
| 8SA-10 | 从动端 | 深沟球轴承 | 307 | 1 |  |
|  | 驱动端 | 深沟球轴承 | 307 | 1 |  |
| 10SA-6 | 从动端 | 单列向心球轴承 | 312 | 1 |  |
|  | 驱动端 | 单列向心球轴承 | 312 | 1 |  |
| 14SA-10 | 从动端 | 单列向心球轴承 | 312 | 2 |  |
|  | 驱动端 | 单列向心球轴承 | 312 | 1 |  |
| 16SA-9 | 从动端 | 滑动轴承 |  |  | 结构三 |
|  | 驱动端 |  |  |  |  |
| 16SA-9 | 从动端 | 深沟球轴承 | 315 | 2 | 结构一 |
|  | 驱动端 | 深沟球轴承 | 315 | 2 |  |
| 20SA-22 | 从动端 | 深沟球轴承 | 312 | 2 |  |
|  | 驱动端 | 深沟球轴承 | 312 | 2 |  |
| 24SA-10 | 从动端 | 深沟球轴承 | 6318 | 1 | 结构二 |
|  | 驱动端 | 深沟球轴承 | 6318 | 1 |  |
| 24SA-18 | 从动端 | 滑动轴承 |  |  | 结构三 |
|  | 驱动端 |  |  |  |  |
| 28SA-9 | 从动端 | 深沟球轴承 | 326 | 2 | 结构二 |
|  | 驱动端 | 深沟球轴承 | 326 | 2 |  |
| 28SA-10 | 从动端 | 深沟球轴承 | 326 | 2 |  |
|  | 驱动端 | 深沟球轴承 | 326 | 2 |  |
| 32SA-10 | 从动端 | 深沟球轴承 | 6328 | 2 |  |
|  | 驱动端 | 深沟球轴承 | 6328 | 2 |  |
| 32SA-19 | 从动端 | 深沟球轴承 | 318 | 1 |  |
|  | 驱动端 | 深沟球轴承 | 318 | 1 |  |
| 32SA-25 | 从动端 | 深沟球轴承 | 318 | 1 |  |
|  | 驱动端 | 深沟球轴承 | 318 | 1 |  |

- The packing sealing consists of packing sleeve, packing ring, packing gland and so on.

The packing boxes are cast in the casing and casing cover. The tightness of the packing should be proper. It is thought fit that the liquid leaks drop by drop. The shaft sleeve will heat if too tight, the liquid will blose excessively. The efficiency of the pump will decrease in either case.

5、Different construction of the bearing

Bearing Type and Specification

| Pump Type | Location | Bearing Name | Specification | Quantity | Bearing Support Type |
| --- | --- | --- | --- | --- | --- |
| 6SA-6 | Driven End | Deep-groove Ball Bearing | 310 | 1 | Fig.1 |
|  | Driving End |  | 310 | 1 |  |
| 6SA-8 | Driven End |  | 308 | 1 |  |
|  | Driving End |  | 308 | 1 |  |
| 8SA-7 | Driven End |  | 309 | 1 |  |
|  | Driving End |  | 309 | 1 |  |
| 8SA-10 | Driven End |  | 307 | 1 |  |
|  | Driving End |  | 307 | 1 |  |
| 10SA-6 | Driven End | Single Centrepelet Ball Bearing | 312 | 1 |  |
|  | Driving End |  | 312 | 1 |  |
| 14SA-10 | Driven End |  | 312 | 2 |  |
|  | Driving End |  | 312 | 1 |  |
| 16SA-9 | Driven End | Sliding Bearing |  |  | Fig.3 |
|  | Driving End |  |  |  |  |
| 16SA-9 | Driven End | Deep-groove Ball Bearing | 315 | 2 | Fig.1 |
|  | Driving End |  | 315 | 2 |  |
| 20SA-22 | Driven End |  | 312 | 2 |  |
|  | Driving End |  | 312 | 2 |  |
| 24SA-10 | Driven End |  | 6318 | 1 | Fig.2 |
|  | Driving End |  | 6318 | 1 |  |
| 24SA-18 | Driven End | Sliding Bearing |  |  | Fig.3 |
|  | Driving End |  |  |  |  |
| 28SA-9 | Driven End | Deep-groove Ball Bearing | 326 | 2 | Fig.2 |
|  | Driving End |  | 326 | 2 |  |
| 28SA-10 | Driven End |  | 326 | 2 |  |
|  | Driving End |  | 326 | 2 |  |
| 32SA-10 | Driven End |  | 6328 | 2 |  |
|  | Driving End |  | 6328 | 2 |  |
| 32SA-19 | Driven End |  | 318 | 1 |  |
|  | Driving End |  | 318 | 1 |  |
| 32SA-25 | Driven End |  | 318 | 1 |  |
|  | Driving End |  | 318 | 1 |  |

三、结构图（Ⅲ Sectional Arrangement Figure）

四、安装、起动、停车和运行

安装

1、安装前的准备工作

（1）检查水泵和电机有无损坏。  （2）按图检查机组的基础。

2、安装要求

（1）泵与电机的轴心线应位于水平面内。

（2）泵与电机的轴心线应在同一直线上。

（3）使泵和电机联轴器之间留3~5毫米间隙。

（4）在泵接上管道后，应按上述要求再校正一次。

起动与停车

1、将轴及其他涂油零件上的油去净。

2、用汽油清洗轴承和油室，用棉纱或破布擦净。

3、装滚珠轴承的泵用黄油作润滑剂，注入轴承时，以占轴承体空间的70%为宜，用稀油润滑的泵，油位应在油标二刻线之间。

4、先取出联轴器的圆柱销，起动电机，检查电机旋转方向，再装好联轴器柱销。

5、经泵盖上方螺孔往泵内灌注水或用真空泵抽除空气引水。

6、闭上吐出管上的闸阀和压力表旋塞。

7、起动电机，打开压力表旋塞。

8、当水泵达到规定转速时，压力表显示相应的压力，然后打开真空气旋塞，并逐渐打开排水管道上的闸阀，调整到需要的压力为止。

- 停止水泵时，要慢慢关闭闸伐和真空计旋塞，然后停止电动机，关闭压力旋塞，若所处环境温度较低时，应将泵体最下方的旋塞打开，放出泵内余水，以免冻裂。

10、当长期停止使用水泵时，应将水泵拆开，擦干零件上的水，并在加工面上涂上防锈油，妥善保存。

运转

1、注意轴承温度，不应超过外界35℃，最高温度不应超过75℃。

2、填料室的漏水以每分钟10~20滴为正常。

3、定期检查弹性联轴器。

4、水泵运行过程中应进行周期性检查。叶轮与密封环间的间隙磨损过大时，应更换叶轮或密封环。

Ⅳ Installation, Start-up, Operation and shut-off

Installation

- Preliminaries before installation

- Inspect whether the pump and the motor are damaged.

- Examine the foundation of the machine unit according to the drawing.

- Requirements in installing

- The axes of the pump and motor must be on the same horizontal plane.

- The axes of the pump and motor must be on the same straight line.

- A certain clearance between the coupling halves of the pump and the motor should be kept in conformity to the drawing.

- Inspection should be repeated in the light of the above requirements after the pump is connected with the pipe lines.

Starting and Stopping

- Remove the grease on the shaft and other oiled parts..

- Cleanse the bearings and oil chambers with gasoline and dry them with cotton waste or rage.

- In respect to the pump with ball bearing lubricated with grease, it is suitable to fill 70% of the rooms of the bearing boxes. The oil level of the pump lubricated with thin oil should be between the two scales on the oil level indicator.

- First, take the coupling pins off; secondly, start the motor to inspect its rotation direction and lastly, put the coupling pins on..

- Fill the pump with water through the hole with screw thread in the upper part of the pump cover prime with a vacuum pump.

- Close the gate valve in the discharge line and the cock in the manometer.

- Start the motor and open the cock in the manometer.

- When the pump runs to a rated speed and the manometer shows a corresponding press-. ure , open the cock in the vacuum gauge and open gradually the gate valve in the disch- arge line until the required pressure is obtained.

- When stop the pump, close slowly the gate valve and the cock in the vacuum gauge; then stop the motor and close the cock in the manometer. If the pump stands an a freezi-

ng temperature, the screw plug in the lowest part of the pump body should be twisted to let the remaining water run out of the pump for preventing cracks due to freezing.

- If the pump is to be idle for long periods, it should be taken apart, dried ,oiled with picking oil on the polished surfaces and preserved judiciously.

Operating

- Care to keep the temperature of the bearing not being 35℃ higher than that in surroun-

Dings and itself not being over 75℃.

- It is normal that the liquid in the stuffing box leaks 10~20 drops pear minute.

- Inspect the elastic coupling periodically.

- In the operation period, the pump should be examined periodically. If the clearance between the impeller and wearing ring is to large, the former or the latter should be replaced.

五、可能发生的故障及其解决的方法

| 故障 | 原因 | 解决方法 |
| --- | --- | --- |
| 1、水泵不吸水，压力表及真空表的指针在剧烈跳动。 | 注入水泵的水不够，水管与仪表漏气。 | 再往水泵注水，拧紧或堵塞漏处。 |
| 2、水泵不吸水真空表指示高度真空。 | 底间没有打开或已污塞，吸水管阻力太大，吸水高度太大。 | 校正或更换底阀，清洗或更改吸水管，降低吸水高度。 |
| 3、看压力表水泵出水处是有压力然而水泵仍不出水。 | 出水管阻力太大，旋转方向不对，叶轮污塞，水泵转速不够。 | 检查或缩短水管及检查电机转向，清洗叶轮，增加水泵的转速。 |
| 4、流量低于预计。 | 水泵污塞或是密封环磨损过多，转速不够。 | 清洗水泵及管子，更换新的密封环，增加水泵的转速。 |
| 5、水泵消耗的功率过大。 | 填料压盖太紧，填料函发热，叶轮损坏了，水泵供水量增加。 | 拧松填料盖或将填料取出来打开一些，更换叶轮，关小闸阀以降低流量。 |
| 6、水泵内部声音反常，水泵不上水。 | 闸门开得太大，吸水管内阻力过大，吸水高度过大，在吸水处有空气渗入，所压送的液体温度过高。 | 关心闸阀以减少流量，检查泵吸水管，检查底阀，减小吸水高度，拧紧或堵塞漏气处，降低液体温度。 |
| 7、水泵振动。 | 泵轴与电机轴不在同一条中心线上。 | 把水泵和电机的轴心线对准。 |
| 8、轴承过热。 | 没有油，水泵轴与电机轴不在一条中心线上，油环不旋转。 | 加油，把轴中心线对准，检查或清洗轴承体。 |

Ⅴ Possible trouble and their remedies

| Trouble | Cause | Remedy |
| --- | --- | --- |
| 1. Pump doesn’t suck, pointers in manometer and vacuum gauge pulsate viol- ently | Water filled into pump insufficient, air leaks in pipe lines and meters. | Refill water into the pump, block leaks. |
| 2. Pump doesn’t suck, Vacuum gague shows high vacuum | Bottom valve is not opened or blocked, resistance in suction line too large, suction head too larhe. | Adjust or replace bottom valve, clean or change suction line, lower suction head. |
| 3. Manometer shows press- ure, but pump delivers no water yet | Resistance in discharge line too large, rotation direction incorrect, impeller blocked, speed of rotation not enough | Inspect or shorten pipe lines and inspect motor rotation direction, clean impeller, increase speed of rotation of pump. |
| 4. Capacity lower than that expected | Pump blocked or wearing ring worn too much, speed of rotation not enough | Clean pump and pipe lines, Replace wearing ring, increase speed of rotation of pump. |
| 5. Power consumed too much | Stuffing gland too tight, stuffing box heated, impeller worn badly, amount of water supply increased. | Loosen stuffing gland or take stuffing off to be squared, replace impeller, adjust gate valve to lower capacity. |
| 6. Pump is noisy and doesn’t suck | Gate valve opened too large, resistance in suction line too large, suction head too large, suction opening, temperature of liquid delivered too high | Adjust gate valve to lower capacity, inspect suction line, inspect bottom valve, lower suction head, block leaks, lower temperature of liquid. |
| 7. Pump vibrates | Shaft centerlines of pump and motor not in alignment. | Align shaft centerline of pump with that of motor. |
| 8. Bearing over heated | No oil, shaft centerlines of pump and motornot in alignment, oil ring doesn’t run | Add oil, align the shaft centerlines, inspect or clean bearing box. |

六、型谱图(Ⅵ Performance Charts)

七、泵性能表(Ⅶ Performance Data)

| 参数 Parameter 型号 Type | 流量 Capacity Q |  | 扬程 Head H | 转速 Speed n | 轴功率 Shaft Power Pa | 配带电动机 Motor |  | 效率 Eff. η | 必需汽蚀余量 (NPSH)r | 叶轮名义直径 Impeller | 泵重 Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | 功率 Power | 型号 Type |  |  |  |  |
|  | m3/h | L/s | m | r/min | kW | kW |  | % | m | mm | kg |
| 6SA-6 (S150-97) | 126 180 216 | 35 50 60 | 104 97 87 | 2980 | 48.8 59.5 64.8 | 75 | Y280S-2 | 73 80 79 | 3 3.8 5.3 | 270 | 150 |
| 6SA-6 (S150-97A) | 119 170 204 | 33 47.2 56.6 | 91 84.5 76 | 2980 | 42 50.1 54.8 | 75 | Y280S-2 | 70 78 77 | 3 3.7 4.7 | 255 | 150 |
| 6SA-6J (S150-97B) | 72 90 108 | 20 25 30 | 24 22.5 20 | 1480 | 6.45 7.45 8.4 | 11 | Y160M-4 | 73 74 70 | 2.6 2.7 2.9 | 205 | 110 |
| 6SA-8 (S150-50) | 108 160 193 | 30 44.5 53.5 | 58 55 52 | 2980 | 24.6 30.1 33.3 | 37 | Y200L2-2 | 69 81 82 | 2.9 3.8 4.4 | 205 | 110 |
| 6SA-8A (S150-50A) | 108 144 174 | 30 40 48.3 | 45 43 39 | 2980 | 18.2 21.1 23.1 | 30 | Y200L1-2 | 73 80 80 | 2.9 3.6 4.1 | 185 | 110 |
| 6SA-8B (S150-50B) | 108 133 160 | 30 36.9 44.5 | 40 38 34 | 2980 | 15.86 17.7 19.4 | 22 | Y180M-2 | 74 78 77 | 2.7 3.1 3.4 | 170 | 110 |
| 8SA-7 (S200-95) | 216 280 336 | 60 77.78 93.5 | 99 95 87 | 2980 | 78.6 90.8 101 | 132 | Y315M-2 | 74 80 79 | 4 4.7 6.6 | 272 | 215 |
| 8SA-7A (S200-95A) | 210 262 314 | 58.4 72.78 87.2 | 87 83 74 | 2980 | 68.1 76.9 83.3 | 110 | Y315S-2 | 73 77 76 | 4 4.5 5.7 | 255 | 215 |
| 8SA-7B (S200-95B) | 190 247 300 | 55 68.61 83.4 | 76 73 63 | 2980 | 57 64.6 71.4 | 75 | Y280S-2 | 72 76 72 | 4 4.2 5.4 | 234 | 215 |
| 8SA-10 | 194 280 351 | 54 77.78 97.5 | 71 63 52 | 2980 | 52 59.3 65.4 | 75 | Y280S-2 | 72 81 76 | 2.8 4.1 5.3 | 235 | 235 |
| 8SA-10A (S200-63A) | 180 259 324 | 50 71.94 90 | 58 52 41 | 2980 | 40.6 46.5 50.2 | 55 | Y250M-2 | 70 79 72 | 2.7 3.8 4.9 | 217 | 235 |
| 8SA-10B (S200-63B) | 173 239 288 | 48 66.4 80 | 48 44 36 | 2980 | 32.2 36.6 38.2 | 45 | Y225M-2 | 70 78 74 | 2.6 3.5 4.2 | 200 | 235 |
| 10SA-6 | 432 540 720 | 120 150 200 | 96 94 89 | 1480 | 152.6 177.2 215 | 250 | Y355M2-4 | 74 78 81 | 5.1 6.3 9.2 | 530 | 600 |
| 10SA-6A | 432 540 720 | 120 150 200 | 85.3 84 76 | 1480 | 129.3 154.5 186.3 | 220 | Y355M2-4 | 77.6 80 80 | 5.1 6.3 9.2 | 500 | 600 |
| 10SA-6B | 432 540 720 | 120 150 200 | 76.4 74 67 | 1480 | 121.5 137.8 164.3 | 185 | Y315M-4 | 74 79 80 | 5.1 6.3 9.2 | 470 | 600 |
| 10SA-6J (10SA-6C) | 400 500 600 | 111.1 138.8 166.6 | 42 39 35 | 980 | 58.7 65.6 72.5 | 90 | Y315M1-6 | 78 81 79 | 3.6 4.7 6.6 | 530 | 600 |
| 10SA-6JA (10SA-6D) | 300 400 500 | 111.1 138.8 166.6 | 36.8 36 33 | 980 | 39.4 49.7 56.2 | 75 | Y315M2-6 | 76.4 79 80 | 3.3 3.6 4.7 | 500 | 600 |
| 10SA-6JB (10SA-6E) | 300 400 500 | 111.1 138.8 166.6 | 33 32 28 | 980 | 34.8 44.1 48.3 | 55 | Y280M-6 | 77.5 79 79 | 3.3 3.6 4.7 | 470 | 600 |
| 10SA-6F | 400 500 600 | 111.1 138.8 166.6 | 66.4 65.6 62.5 | 1480 | 95.2 113.1 131 | 160 | Y315L1-4 | 76 79 78 | 4.6 5.7 7.5 | 436 | 600 |
| 14SA-10 | 900 1080 1260 | 250 300 350 | 70 68 64 | 1480 | 206.5 230 250 | 315 | Y355L2-4 | 83 87 88 | 4.1 4.6 5.4 | 466 | 1210 |
| 14SA-10A | 900 1080 1260 | 250 300 350 | 60 58 54 | 1480 | 175 196 213 | 250 | Y315 M2-4 | 84 87 87 | 5.1 6.3 6.9 | 440 | 1210 |
| 14SA-10B | 900 1080 1260 | 250 300 350 | 51 48 44 | 1480 | 149 162.2 179.7 | 220 | Y335M1-4 | 84 87 84 | 5.1 6.3 6.9 | 425 | 1210 |
| 14SA-10J (14SA-10C) | 650 800 1000 | 180.56 222.22 277.78 | 30 28 24 | 980 | 66.6 72.6 78.7 | 90 | Y315M-6 | 79.7 84 83 | 1.79 2.21 3.16 | 466 | 1210 |
| 14SA-10JA (14SA-10D) | 600 720 900 | 166.6 200 250 | 27 25 22 | 980 | 54.9 57.9 64.2 | 75 | Y315S-6 | 81 84.6 84.2 | 1.69 2.06 2.75 | 440 | 1210 |
| 14SA-10JB (14SA-10E) | 600 720 900 | 166.6 200 250 | 23 21 18 | 980 | 44.2 47.3 53.1 | 75 | Y315S-6 | 85 87 83 | 4 4 4.1 | 425 | 1210 |
| 14SA-10F | 450 547 684 | 125 152 190 | 15.6 14.5 12.7 | 742 | 22.75 25.1 27.8 | 37 | Y280S-8 | 84 86 85 | 5.8 5.8 5.8 | 440 | 1210 |
| 16SA-9 | 1080 1260 1620 | 300 350 450 | 97.6 96 90 | 1480 | 400 428 473 | 630 | Y450-4 | 71.6 77 84 | 5.2 5.9 7.9 | 535 | 1910 |
| 16SA-9A | 1080 1260 1620 | 300 350 450 | 85.8 85 78 | 1480 | 346 370 410 | 450 | Y400-4 | 73 79 84 | 5.2 5.9 7.9 | 510 | 1910 |
| 16SA-9B | 1080 1260 1620 | 300 350 450 | 78 76 68 | 1480 | 298 318 349 | 450 | Y400-4 | 77 82 86 | 5.2 5.9 7.9 | 480 | 1910 |
| 16SA-9J (16SA-9C) | 900 1080 1260 | 250 300 350 | 40 40 38 | 980 | 124 140 155.3 | 185 | Y355M2-6 | 79 84 84 | 1.79 2.33 2.84 | 535 | 1910 |
| 16SA-9JA (16SA-9D) | 900 1080 1260 | 250 300 350 | 37 35 32 | 980 | 112 123 131 | 160 | Y355M1-6 | 81 84 84 | 4.6 4.9 5.2 | 510 | 1910 |
| 16SA-9JB (16SA-9E) | 800 900 1080 | 222.22 250 300 | 33 32 30 | 980 | 89 95 102.5 | 110 | Y315L1-6 | 80 83 86 | 4.6 4.6 4.9 | 480 | 1910 |
| 20SA-22 | 1368 1980 2304 | 380 550 640 | 26.5 21 17.5 | 980 | 122 133.2 137.2 | 160 | Y315M1-6 | 80 85 80 | 4.4 5.2 5.8 | 466 | 1610 |
| 20SA-22A | 1260 1800 2088 | 350 500 580 | 21 16 12.4 | 980 | 90 92.3 88.1 | 110 | Y315L1-6 | 80 85 80 | 4.3 4.9 5.4 | 425 | 1610 |
| 20SA-22J (20SA-22B) | 1080 1450 1800 | 300 402.7 500 | 16.3 14 10.7 | 742 | 61.5 65 66.8 | 90 | Y315L1-8 | 78 85 78.5 | 2.8 4 7.1 | 458 | 1610 |
| 20SA-22JA (20SA-22C) | 1080 1300 1627 | 300 361 452 | 10.3 9.5 6.8 | 742 | 37 41 38.6 | 55 | Y315S-8 | 82 85 78 | 2.8 3.5 5.6 | 425 | 1610 |
| 24SA-10 | 2592 3420 3600 | 720 950 1000 | 78 71 69 | 990 | 643.9 738.8 760 | 900 | Y5003-6 | 85.5 89.5 89 | 5.6 5.9 8.2 | 725 | 4100 |
| 24SA-10J (24SA-10A) | 2160 2700 2970 | 600 750 825 | 43 39 36 | 742 | 290.7 322.2 334.6 | 400 | Y4503-8 | 87 89 87 | 5.6 5.9 8.2 | 725 | 4100 |
| 24SA-10B | 2338 3084 3248 | 649 856.6 902.2 | 63.5 57.8 56.2 | 990 | 472.8 545.4 558.5 | 630 | Y4504-6 | 85.5 89 89 | 4.6 7.3 8.2 | 655 | 4100 |
| 24SA-18 | 2700 3240 3600 | 750 900 1000 | 35.1 32.6 29.76 | 980 | 310.9 330.1 341.2 | 400 | Y4005-6 | 83.1 87 85.5 | 4.5 5.15 6.12 | 550 | 3300 |
| 24SA-18A | 2520 3000 3165 | 700 833.3 879 | 25.5 23 19.2 | 980 | 206 211 204 | 250 | Y355L2-6 | 85 89 84 | 6 6.4 81 | 490 | 3300 |
| 24SA-18J (24SA-18B) | 2052 2466 2836 | 570 685 787 | 20.3 18.9 16.1 | 742 | 136.6 145.6 147.4 | 160 | Y355M-8 | 83.1 87.2 84.4 | 2.83 3.19 4.03 | 550 | 3300 |
| 24SA-18JA (24SA-18C) | 1908 2000 2520 | 530 555.5 700 | 14.7 13.5 11.2 | 742 | 90 86.5 88.3 | 110 | Y315L2-8 | 84.5 85 87 | 3.2 3.7 4.4 | 490 | 3300 |
| *24SA-18D | 2160 3240 3450 | 600 900 958 | 23.2 16 14.2 | 742 | 166 166 163 | 200 | Y400-8 | 82 85 81.6 | 4.7 5.1 5.5 | 539 | 3300 |
| 24SA-18F | 1800 3000 3375 | 500 833 937 | 33.3 26.6 23.3 | 980 | 242.2 263.3 263.7 | 280 | Y4002-6 | 67.4 82.7 81.2 | 4.56 3.97 6 | 510 | 3300 |
| 28SA-9 | 3700 4700 4896 | 1028 1306 1360 | 99.5 90 87.7 | 980 | 1164 1280 1305 | 1600 | Y6301-6 | 86.1 90 89.6 | 7.87 9.25 10 | 840 | 6800 |
| 28SA-9J | 2111 3600 4200 | 586 1000 1167 | 60.1 52 43.8 | 740 | 432 569 604 | 630 | Y560-8 | 80 89.6 83 | 4.4 5.4 8.9 | 840 | 6800 |
| 28SA-10 | 4536 5292 6350 | 1260 1470 1764 | 94 90 97 | 980 | 1451 1544 1624 | 1800 | Y6302-6 | 80 84 82 | 8 10.4 14.8 | 840 | 5800 |
| 28SA-10A | 4185 4882.5 5859 | 1162 1356 1627 | 80 76.6 65.5 | 980 | 1169 1227 1275 | 1400 | Y630-6 | 78 83 82 | 7.2 9.2 13.2 | 775 | 5800 |
| 28SA-10J | 3362 3922 4707 | 933.9 1089 1307 | 51.6 49.4 42.3 | 742 | 590 628 661 | 710 | Y560-8 | 80 84 82 | 5.8 6.8 9.2 | 840 | 5800 |
| 28SA-10JA | 3102 3618 4343 | 862 1005 1206 | 43.9 42 36 | 742 | 463 498 519 | 630 | Y560-8 | 80 83 82 | 5.6 6.1 8 | 775 | 5800 |
| *28SA-10K | 2736 3600 4140 | 760 1000 1150 | 53 51 47 | 742 | 556 617 646 | 710 | Y560-8 | 71 81 82 | 4 5 6 | 848 | 5800 |
| 32SA-10 | 6300 8280 9900 | 1750 2300 2750 | 73.5 67.5 57.5 | 742 | 1510 1720 1856 | 2240 | Y710-3-8 | 83.5 88.5 83.5 | 5.9 7 8.5 | 990 | 8300 |
| 32SA-10B | 5940 7920 9540 | 1650 2200 2650 | 67.8 62.5 52.5 | 742 | 1321 1523 1643 | 1800 | Y710-1-8 | 83 88.5 83 | 5.8 6.7 8.5 | 950 | 8300 |
| 32SA-10C | 5760 7200 8820 | 1750 2300 2750 | 59 53.5 46.5 | 740 | 1128.6 1213 1370 | 1600 | Y630-8 | 82 86.5 81.5 | 5.7 6.3 7.5 | 885 | 8300 |
| 32SA-10J | 4860 6480 8100 | 1350 1800 2250 | 48.3 44.2 35.5 | 590 | 780 881 960 | 1120 | Y630-10 | 82 88.5 81.5 | 3.7 4.2 5.3 | 990 | 8300 |
| 32SA-10JB (32SA-10D) | 4680 6300 7740 | 1300 1750 2150 | 44 40.5 33 | 590 | 684 785 848 | 1000 | Y630-10 | 82 88.5 82 | 3.6 4 5 | 950 | 8300 |
| 32SA-10JC | 3960 5400 6480 | 1100 1500 1800 | 31.5 28.5 24 | 495 | 414 474 510 | 560 | Y560-12 | 82 88.5 83 | 2.8 3.1 3.6 | 885 | 8300 |
| 32SA-19 | 4390 5400 5760 | 1219 1500 1600 | 33.3 29 26.3 | 742 | 470 473.8 485.3 | 560 | Y5002-8 | 84.6 90 85 | 6.3 8.2 10.3 | 708 | 6000 |
| 32SA-19A | 4170 5000 5470 | 1158 1388 1519.4 | 29.3 26 23.7 | 742 | 391 393.3 415.3 | 500 | Y5001-8 | 85 90 85 | 6.1 7.2 9.3 | 670 | 6000 |
| 32SA-19B | 3654 4700 5220 | 1015 1305.5 1450 | 23.7 20 17 | 742 | 275.8 284.5 282 | 355 | Y450-8 | 85.5 90 85.5 | 6 6.3 8.2 | 616 | 6000 |
| 32SA-19E | 4320 5278 6034 | 1200 1466 1676 | 36.8 33.8 29.6 | 740 | 512.3 545.8 559 | 630 | Y560-8 | 84.5 89 87 | 5.9 6.4 9.4 | 730 | 6000 |
| 32SA-19J | 3456 4320 4615 | 960 1200 1282 | 21.6 18.6 17 | 590 | 231.1 243.1 254 | 280 | Y450-10 | 87.8 90 84.1 | 3.5 5 6.4 | 708 | 6000 |
| 32SA-19JA (32SA-19C) | 3240 4000 4320 | 900 1111 1200 | 19.1 16.5 15.2 | 590 | 192.6 199.7 204.3 | 250 | Y450-10 | 87.5 90 87.5 | 4 4.5 6.1 | 668 | 6000 |
| 32SA-19JB (32SA-19D) | 2880 3800 3960 | 800 1055 1100 | 15.8 13 11.8 | 590 | 146.6 151.1 147.1 | 200 | Y400-10 | 84.5 89 86.5 | 3.9 4 4.4 | 610 | 6000 |
| 32SA-19F | 3726 4705 5407 | 1035 1307 1502 | 26.5 23 19 | 742 | 323.9 335 341.1 | 400 | Y450-8 | 83 88 82 | 6.1 7.4 9.2 | 630 | 6000 |
| 32SA-25 | 4320 5400 6300 | 1200 1500 1750 | 25.2 22.3 17.4 | 742 | 352 367 364 | 400 | Y4503-8 | 84 89.3 82 | 6.1 7.4 9.2 | 620 | 6000 |
| 32SA-25J | 3240 4140 5040 | 900 1150 1400 | 16.6 15 11.5 | 595 | 179.7 190 190.2 | 250 | Y4502-10 | 81.5 89 83 | 4.0 4.9 6.8 | 620 | 6000 |

带“*”号的泵模型不同