LC型立式长轴泵

安装使用说明书

长沙福斯水泵泵业有限公司

概述   General

LC型立式长轴泵是在吸收国内外设计和制造先进经验的基础上，结合市场需求研制的先进成熟的系列产品。输送清水和含一定固体颗粒（如铁屑、砂粒、煤粉等）的污水、具腐蚀性工业废水、海水；输送液体温度不超过80℃。广泛用于原生水处理厂、污水处理厂、冶金钢铁行业（特别是该行业漩流池输送氧化铁皮）、电厂、矿山、市政工程及农田水利工程。

Type LC vertical long-shaft pump is a newly developed product with both homeland and overseas advanced experience in design and manufacture. It is used to deliver clear water, sewage with certain solid particles (such as iron scrap, sand, coal powder etc.) and industry waste water and seawater with corrosive. The temperature of liquid can not be above 80℃. It is widely used in original water works, waste water factory, metallurgy and steel industry (especially suitable for delivering oxygenation iron sheet water in swirl pool), power station，mine, civil project and farmland etc.

型号意义  Type Description

300LC2-50A

300—泵出口直径为φ300mm           Outlet diameter of pump is 300mm

LC—立式长轴泵                      Vertical long-shaft pump

2—叶轮级数为2级（级数为1时略）    Impeller stage number (No indication, when

stage number is 1)

50—设计点扬程为50m                 The head is 50m at design point

A—叶轮外径切割代号                 The cut code of impeller

性能范围（设计点） Range of performance (Design point)

流量 Capacity：60~8400m3/h

扬程：Head:  12.5~94.5m

结构特点 Construction feature

LC型立式长轴泵入口垂直向下，出口水平，单基础安装，泵和电机直联；从电机端俯视，泵为逆时针方向旋转，主要特点有：

1．用水力设计软件优化设计，性能优越，并充分考虑了叶轮及导叶的抗磨蚀性，使叶轮等易损件寿命大大提高；产品运行平稳、安全可靠、高效节能。

2．水泵进口装有滤网，开孔大小适当，既有效地防止大颗粒杂质进入泵内损坏水泵，同时又保证了净进水面积是扬水管断面面积的3.5倍以上，最大限度地减少了进口损失，提高了水泵效率。

3．叶轮采用平衡孔平衡轴向力，叶轮前后盖板均设有可更换的密封环，保护叶轮及泵体。密封环采用特殊堰堤型结构，可有效防止泵停机后氧化铁皮或其它杂质沉至密封环间隙进口处，极大地提高了密封环和叶轮的使用寿命。

4．泵中间轴、扬水管和护管为多节，中间接轴采用套筒联轴专利技术，径向同轴度比其它联轴方式提高十倍，整机振动减少70%以上；扬水管数量可根据用户需要增减，适应不同的液下深度。叶轮、导叶体可为多级，适应不同的扬程要求。

5．水泵扬水管由法兰连接，中间有导轴承。水泵导轴承采用加强型填充聚四氟乙烯或加拿大赛龙轴承，也可采用丁腈橡胶（用于介质温度高于55℃），轴由护管保护。当输送清水时，可取消护管，导轴承不必接冷却润滑水；输送污水时，导轴承须外接冷却润滑水。对现场没有清洁水或清洁水成本较高的地方，可增设特殊结构，采用泵输送的介质经过过滤或沉淀分离后对导轴承进行冷却润滑。润滑水系统可增设流量及压力继电器等控制元件，开机前供水量低于额定供水量时，泵不能起动，当运行过程中由于某种原因（管路堵塞）造成缺水，缺压时，继电器发出报警信号，控制室蜂鸣器鸣叫，红灯报警，此时可打开旁通系统的阀门供水，保证供水充分，同时可对故障进行检修，这一控制系统可实现远程摇控。

6．泵的残余轴向力和转子部件的重量由电机座内的推力轴承承受或带推力轴承的电机承受。推力轴承用稀油润滑，并外接水进行冷却。推力轴承可埋设温控元件。

7．泵的轴封为填料密封，轴封及导轴承处装有可更换的轴套，以保护轴。叶轮的轴向位置由轴承部件上端或泵联轴器内的调整螺母来调整，十分方便。

8．水泵可配备控制柜，它具有根据液位自动启停和过载报警及实时远程监控等多种功能，可实现多泵联网远程集中控制。口径大于500mm的泵设有自动排气系统。

The type LC vertical long-shaft pump is installed with single foundation, its inlet is vertical downward and outlet is horizontal. The pump and the motor are directly connected. The rotation of pump rotor is counter clockwise looking from the motor to the pump; the main features are as following

- It is fine designed with hydraulic design software. It makes impeller and other wearing parts have a long life because of anti-abrasive impeller and Diffuser. The pump is not only reliable, safe, steady but also saving energy.

- There is filter in pump inlet with proper hole, this can not only prevent impurity entering pump to damage pump but also decrease inlet loss and increase pump efficiency.

- Impeller adopts balance hole to balance axial force. There is replaceable seal ring in front and back cover board of impeller to protect impeller and pump.

- Pump middle shaft, water column and guard pipe are multi-burl, middle shaft uses technology of sleeve coupling. Water pipe can be more or less for different inundated depth according to user’s requirement. Impeller and Diffuser are multi-stage for different head.

- Water pipe is connected by flange with guide bearing in its middle. Pump guide bearing adopts ethane or THORDON bearing, it can also adopt rubber (when the temperature of liquid is over 55℃).Shaft is protected by guard column, the guide bearing should be supplied with exterior cooling lubricating water, while delivering sewage.

- The remaining axial force of pump and the weight of rotor parts are borne by thrust bearing in motor seat or motor with thrust bearing. The thrust bearing is lubricated by dilute oil and cooled with exterior water. The thrust bearing can have element for monitoring temperature.

- Pump shaft seal adopts packing seal, there is replaceable shaft sleeve in shaft seal and guide bearing to protect shaft and it is convenient to adjust axial location of impeller by nut in bearing parts upper end or pump coupling.

- Pump can be equipped with controller which can automatically start and stop pump according to liquid level, give an alarm for over loading and control many pumps in long-distance. There is automatic exhaust system for pump with diameter over 500mm.

主要零件材料表 Material of main Parts

| 输送介质Pumped Medium 材料类别Material Sort 零件名称Part Name | 清水 Clear Water | 污水 Sewage | 海水Seawater |  |
| --- | --- | --- | --- | --- |
|  | Ⅰ | Ⅱ | Ⅲ | Ⅳ |
| 喇叭口 Bell Mouth | HT250 | HT250 | HT250Ni2Cr | ZG00Cr17Ni14Mo2 |
| 叶 轮 Impeller | HT250 | ZG1Cr13Ni1或 ZG1Cr18Ni9 | ZG00Cr17Ni14Mo2 | ZG00Cr17Ni14Mo2 |
| 导叶体 Diffuser | HT250 | QT500-7 | HT250Ni2Cr | ZG00Cr17Ni14Mo2 |
| 扬水管 Water Column | Q235-A | Q235-A | HT250Ni2Cr | ZG00Cr17Ni14Mo2 |
| 出水弯管 Discharge Elbow | Q235-A | Q235-A | HT250Ni2Cr | ZG00Cr17Ni14Mo2 |
| 护 管 Guard Column | Q235-A | Q235-A | 1Cr18Ni9 | 00Cr17Ni14Mo2 |
| 轴 Shaft | 45或2Cr13 | 45或2Cr13 | 1Cr18Ni9 | 1Cr18Ni9 |
| 轴 套 Shaft Sleeve | 2Cr13 | 2Cr13 | 1Cr17Ni2 | 1Cr17Ni2 |
| 导轴承 Guide Bearing | 填充聚四氟乙烯或赛龙Filling in ethane or Thordon |  |  |  |
| 导轴承体 Guide Bearing Body | HT250 | HT250 | HT250Ni2Cr | ZG00Cr17Ni14Mo2 |
| 密封环 Sealing Ring | HT250 | 2Cr13 | HT250Ni2Cr | ZG00Cr17Ni14Mo2 |
| 套筒联轴器 Adapter Coupling | 45或2Cr13 | 45或2Cr13 | 1Cr17Ni2 | 1Cr17Ni2 |
| 联轴器 Coupling | HT250 | HT250 | HT250 | HT250 |
| 电机座 Motor Support | Q235-A | Q235-A | Q235-A | Q235-A |

注：材料可根据用户要求选配。

Remarks: Other materials can be used according user’s requirement.

型谱图

Available Head-Capacity Curves

结构图

Structure Drawing

1 弹性联轴器  Flexibility Coupling

2 电机座      Motor Support

3 推力轴承座  Thrust Bearing Parts

4 密封部件    Sealing parts

5 传动轴      Driver Shaft

6 出水弯管    Discharge Elbow

7 底座        Foundation Support

8 调整护管    Adjust Guard Column

9 调整扬水管  Adjust Water Column

10 护管       Guard Column

11 中间轴     Middle Shaft

12 导轴承体   Guide Bearing Body

13 扬水管     Water Column

14 套筒联轴器 Adapter Coupling

15 导轴承     Guide Bearing

16 轴套       Shaft Sleeve

17 末级导叶体 The End Diffuser

18 叶轮轴     Impeller Shaft

19 首级导叶体 The First Diffuser

20 密封环     Wearing

21 叶轮       Impeller

22 喇叭口     Bell Mouth

23 滤网       Filter

性能参数表

Sheet of Performance Date

性能参数表

Sheet of Performance Date

性能参数表

Sheet of Performance Date

性能参数表

Sheet of Performance Date

性能参数表

Sheet of Performance Date

性能参数表

Sheet of Performance Date

性能参数表

Sheet of Performance Date

性能参数表

Sheet of Performance Date

性能参数表

Sheet of Performance Date

性能参数表

Sheet of Performance Date

性能参数表

Sheet of Performance Date

注：N为扬水管节数

选型说明

Description

1.泵的性能参见泵的性能参数表,表中所列参数为一个大气压下常温清水不含扬水管和滤网的试验性能,计算装置扬程时,扬水管和滤网的损失按每10m损失1.5m计算。

2. 电机系按γ≤1100Kg/cm3配制，YLS系6KV电机，根据需要可配10KV电机。

3. 订货时需注明泵的型号、参数、材料以及液下深度。

4. 输送介质温度大于55°时需注明

1. Pump performance refer to “Sheet of Performance Date”. The date in sheet is test performance in a atmosphere & normal temperature & clear water, not including loss of water column and filter. Calculating installation head, the head loss of the water column and filter to be calculated is by 1.5m loss per 10m length.

2. Motor is selected by gravity ≤1100Kg/cm3 , the motor of YLS is for 6KV. The motor of 10KV can also be equipped if necessary.

3. The pump type, performance, material, submerged depth must be stated in order.

4. It must be stated when the temperature of medium is over 55°.

成套供货范围  Supply Range of Complete Set

| 序号 No. | 名称 Name | 序号 No. | 名称 Name |
| --- | --- | --- | --- |
| 1 | 水泵 Pump | 4 | 润滑水控制系统 Lubricating Water Controlling System |
| 2 | 立式电机 Vertical Motor | 5 | 备品备件 Spare Parts |
| 3 | 地脚螺栓、专用工具 Foundation bolts, Special Wrench | 6 | 控制柜 Control Cabinet |

注：1、2、3项为必供项，4、5、6项为选择项。

Remarks: Items of 1,2,3 must be provided ,Item of 4,5,6 are option.

外形安装图

Overall installing dimension Drawing

外形安装尺寸表

Overall installing dimension Sheet

外形安装尺寸表

Overall installing dimension Sheet

外形安装尺寸表

Overall installing dimension Sheet

外形安装尺寸表

Overall installing dimension Sheet

N为杨水管节数，L1为调整扬水管长度，每100mm为一档。

泵出口法兰尺寸 Flange Size Sheet of Inlet & Outlet

| 泵口径 Pump Diameter | DN | D4 | D5 | n—d |
| --- | --- | --- | --- | --- |
| 150 | φ150 | φ240 | φ285 | 8-φ22 |
| 200 | φ200 | φ295 | φ340 | 8-φ22 |
| 250 | φ250 | φ350 | φ395 | 12-φ22 |
| 300 | φ300 | φ400 | φ445 | 12-φ22 |
| 350 | φ350 | φ460 | φ505 | 16-φ22 |
| 400 | φ400 | φ515 | φ565 | 16-φ26 |
| 450 | φ450 | φ565 | φ615 | 20-φ26 |
| 500 | φ500 | φ620 | φ670 | 20-φ26 |
| 600 | φ600 | φ725 | φ780 | 20-φ30 |
| 700 | φ700 | φ840 | φ895 | 24-φ30 |
| 800 | φ800 | φ950 | φ1015 | 24-φ33 |
| 900 | φ900 | φ1050 | φ1115 | 28-φ33 |
| 1000 | φ1000 | φ1160 | φ1230 | 28-φ36 |

安装

1．泵安装的好坏，对泵的平稳运行和使用寿命，有很重要的影响，所以安装校正工作必须仔细地进行，不得草率行事。

2．排出管路应有支架，泵不允许承受管路的负荷。

3．安装泵的地点应足够宽敞，以方便检修工作。

4．安装顺序

a．将底座放在有地脚螺栓的基础上，底座与基础之间加成对的楔垫。将水平仪放在底座上，通过调整楔垫，校正水平，拧紧地脚螺栓，以防走动。

b．用混凝土灌注底座和地脚螺栓。

c．待混凝土干固后，检查底座水平度和地脚螺栓有无松动。

d．将机组吊放到底座上，并连接成整体，配置好冷却水管。

e．通过调整推力轴承上部或泵联轴器内的调整螺母来提升转子，转子提升量为转子总窜量的1/2。

f．通过调整电机座上的顶丝来调整电机联轴器的中心。

g．检查联轴器的跳动，对刚性联轴器，水泵的电机联轴器径向跳动和端面跳动小于0.10mm，对弹性联轴器，水泵和电机联轴器，水泵和电机联轴器径向偏差和端面间隙符合下表的规定。

单位：mm

| 联轴器外径 | 170 | 190 | 220 | 260 | 330 | 410 | 640 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 两联轴器径向偏差 | 0.07 | 0.08 | 0.08 | 0.08 | 0.09 | 0.1 | 0.1 |
| 两联轴器端面间隙 | 4 | 4 | 4 | 5 | 6 | 7 | 8 |

5．水泵与出水管路之间，一般需装闸阀和止回阀，闸阀装在泵和止回阀之间。

Installing

1. Pump installing quality is affected directly on pump running and life. So installing and adjusting must be strict.

2. Discharge pipe should have itself support, the pump don’t allow bearing pipe weight.

3. The place of installing pump should be enough wide, to insure to repair conveniently.

4. Sequence of installing

a. Place the pump base on foundation with foundation bolts. Add the couple wedge between foundations and pump base. Put the gradienter on base; adjust the base level through the wedge. Screw the bolts to protect moving.

b. Pour concrete into foundation and foundation bolt hole. (Foundation usually have ready hole, adopt second pouring to fill up.)

c. After concrete dry, check and ensure the base and foundation tight. Screw up foundation nuts, check the level degree again.

d. Put the pump set on foundation base, and joint them together. Assemble the cooling pipe.

e. Adjust the rotor height through adjust nut up the thrust force bearing or in coupling, the lift height of rotor is 1/2 of total change value of rotor.

f. Adjust the coupling center through adjusting locating nut.

g. Check the coupling pulsate degree, to rigid coupling, the value of coupling radial pulsate and endface pulsate of pump and motor is ≤0.1mm. to flexible coupling, the radial tolerance and endface clearance of pump and motor should be satisfy the requirement as follows:

Unit: mm

| The outer circle diameter of coupling | 170 | 190 | 220 | 260 | 330 | 410 | 640 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| The radial tolerance between coupling | 0.07 | 0.08 | 0.08 | 0.08 | 0.09 | 0.1 | 0.1 |
| Th endface clearance between coupling | 4 | 4 | 4 | 5 | 6 | 7 | 8 |

5. Between pump and discharge pipe, the fate valve and check fate will be installed, the check valve install between fate valve and pump discharge.

起动、停止和运行

1．起动与停止

a．起动前，检查电机的转向，看是否与旋转方向一致；扳动泵轴，应转动灵活。

b．起动前检查基础螺栓有无松动，以及润滑油和冷却水供应情况，冷却水为清洁软水，导轴承润滑水压力和流量见附表。推力轴承冷却水流量0.3～0.5m3/h，压力0.1～0.2MPa。

特别提醒：泵冷却水压力及流量不足，对泵使用寿命有严重影响。

c．关闭出口闸阀和压力表旋塞，接通泵的冷却润滑水。

d．两分钟后启动电机，逐渐打开出口闸阀和压力表旋塞，调节到所需工况。

e．当要停止水泵运转时，逐渐关闭出口闸阀和压力表的旋塞，然后切断电源。

f．泵完全停止转动后，再关闭冷却润滑水。

2．运行

a.经常检查轴承发热情况，水泵轴承温度不应超过75℃，并随时检查油杯的油位，定期加油。如发现润滴油有乳化现象，应及时更换。

b．经常检查润滑水流量及压力，运行中绝不允许断水，对带过滤装置的润滑系统，需定期清洁过滤网。

c．经常检查密封的泄漏和发热情况。若泄漏过大，应更换填料。

d．定期检查联轴器同心度，注意电机轴承温升。

e．运转过程中，如发现噪音或其它不正常的声音时，应立即停止，检查其原因，加以消除。

f．不得在泵允许的范围外运行，以免过载烧坏电机。

g．不得在泵淹深不够的情况下运行，以免发生汽蚀损坏水泵。

Starting, Running & Stopping

1 Starting & Stopping

a. Before starting, check the motor rotating direction., pump rotating is flexible by hand.

b. Before starting, check the nut and insure them tightly, and lubricating oil and cooling water supply steadily, the cooling water should be clear water. The pressure and flow see attached sheet

Specially note: the pressure of cooling water and flow is not enough, it will effect the pump life greatly.

c. Shut off fate valve on discharge pipe and nut of manometer, switch on the cooling water pipe.

d. After starting the pump for 2 minutes, slowly shut on the fate valve and nut manometer on discharge pipe, adjust them to the required condition.

e. g  Before stop the pump, slowly shut off the fate valve on discharge pipe and nut of manometer. Then shut off the power source.

f. When the pump stop entirely, then shut off the cooling water.

2 Running

a. During running, check the bearing temperature timely. Max. bearing temperature is not more than 75ºC  packing leakage flow, and overheated, and pump vibrate, noise etc. if the condition is not normal,  treat it in time.

b. Check the lubricating water pressure and flow , the lubricating water should not be allow to interrupt, to lubricating system with strainer, the strainer should be cleaned timely.

c. Timely check the coupling centering degree, and watch the bearing temperature rise.

d. In operating, if pump have voice or other abnormal voice, the pump should be shut off. Found the reason and clean out

e. Pump don’t allow to operate out of permitted range, escape to damage the motor.

f. The pump don’t allow operating without enough submerged height.

导轴承润滑水流量、压力

Pressure and Capacity of lubricating water

| 泵型号 Pump Type | 润滑水压力（MPa） Lubricating Water Pressure | 润滑水流量（m3/h） Lubricating Water Capacity |
| --- | --- | --- |
| 150LC23、23A | 0.3～0.4 | 0.8～1.0 |
| 150LC-30、30A | 0.4～0.5 |  |
| 150LC2-46、46A | 0.6～0.7 |  |
| 150LC2-60、60A | 0.7～0.8 |  |
| 150LC3-90、90A | 1.0～1.1 |  |
| 200LC-19、19A、23 | 0.2～0.3 |  |
| 200LC2-38、38A、46 | 0.3～0.4 |  |
| 200LC3-57 | 0.5～0.6 |  |
| 200LC3-69 | 0.6～0.7 |  |
| 200LC4-92 | 0.7～0.8 |  |
| 200LC-20、20A | 0.2～0.3 | 1.2～1.4 |
| 250LC-32、32A、 250LC2-40 | 0.3～0.4 |  |
| 250LC2-63、63A | 0.4～0.5 |  |
| 250LC3-95、95A | 0.7～0.8 |  |
| 300LC-25、25A | 0.2～0.3 |  |
| 300LC-39、39A | 0.4～0.5 |  |
| 300LC2-50、50A | 0.3～0.4 |  |
| 300LC2-78、78A | 0.5～0.6 |  |
| 350LC-19、19A | 0.2～0.3 | 1.4～1.6 |
| 350LC-30、30A、30B | 0.3～0.4 |  |
| 350LC-48、48A、48B | 0.5～0.6 |  |
| 350LC2-60、60A、60B | 0.4～0.5 |  |
| 400LC-25、25A | 0.2～0.3 |  |
| 400LC-39、39A | 0.4～0.5 |  |
| 400LC2-50、50A | 0.3～0.4 |  |
| 400LC-62、62A、62B | 0.6～0.7 |  |
| 450LC-17、17A | 0.2～0.3 | 1.6～1.8 |
| 450LC-27、27A、27B | 0.3～0.4 |  |
| 450LC-43、43A、43B | 0.5～0.6 |  |
| 450LC2-54、54A | 0.4～0.5 |  |
| 500LC-20、20A | 0.2～0.3 | 1.8～2.0 |
| 500LC-31、31A、31B | 0.3～0.4 |  |
| 500LC-50、50A、50B | 0.5～0.6 |  |
| 500LC2-63、63A | 0.4～0.5 |  |
| 600LC-25、25A | 0.2～0.3 |  |
| 600LC-39、39A、39B | 0.4～0.5 |  |
| 600LC-62、62A、62B | 0.6～0.7 |  |
| 700LC-20、20A | 0.2～0.3 | 2.2～2.4 |
| 700LC-32、32A、32B | 0.3～0.4 |  |
| 700LC-50、50A、50B | 0.5～0.6 |  |
| 800LC-24、24A | 0.2～0.3 |  |
| 800LC-38、38A、38B | 0.4～0.5 |  |
| 800LC-60、60A、60B | 0.6～0.7 |  |
| 900LC-21、21A | 0.2～0.3 | 2.6～2.8 |
| 900LC-33、33A、33B | 0.4～0.5 |  |
| 900LC-52、52A、52B | 0.5～0.6 |  |
| 1000LC-25、25A | 0.2～0.3 |  |
| 1000LC-39、39A、39B | 0.4～0.5 |  |
| 1000LC-63、63A、63B | 0.6～0.7 |  |

常见故障、原因及消除方法

| 常见故障 | 原因 | 消防方法 |
| --- | --- | --- |
| 起动不起来 | - 电机或供电系统故障 - 转子部件中有异物 - 轴承被卡住 - 起动条件不满足 | - 检修电机或供电系统 - 清理转子部件 - 清理或更换轴承 - 检查应满足的条件 |
| 流量不足或不出水 | - 吸入侧或出口侧或叶轮有杂物堵塞 - 密封环磨损过多或叶轮损坏 - 转向不对 - 转速过低 - 淹深不够，吸入空气 | - 清理滤网、叶轮、导叶体、排出管、阀系统 - 更换损坏的零件 - 校正转向 - 测量电压、频率、检查电机 - 提高吸入水位 |
| 超负荷 | - 轴承损坏（包括导轴承） - 泵内有异物 - 叶轮与密封环有磨擦 - 填料压得过紧 - 转速过快 - 泵超运行范围，大流量运行 - 供电线一相断路，单相运行 | - 更换轴承 - 清除异物 - 调整间隙 - 放松填料 - 检查电压、频率、电机，并作调整 - 关小出口闸阀 - 专业人员检查、修理 |
| 异常振动和噪音 | - 淹深不够，泵发生汽蚀 - 叶轮不平衡 - 轴不同心或轴弯曲 - 基础螺栓松动 - 轴承损坏 - 导轴承及轴套磨损，间隙增大 - 排出管路的影响 | - 提高吸入水位或关小出口闸阀 - 叶轮校正静平衡 - 校正轴的同心度，校直轴 - 拧紧地脚螺栓 - 更换轴承 - 更换导轴承及轴套 - 检查和排除影响 |
| 轴承发热 | - 装配不良，轴心偏心过大 - 轴承损坏 - 轴承内没有油 | - 检查径向跳动，进行校正 - 更换轴承 - 加润滑油 |

Troubles & Causes & Remedies

| Troubles | Causes | Remedies |
| --- | --- | --- |
| Pump doesn’t start up. | - Motor or power system have some troubles; - Some impurity in rotor; - Bearing is locked; - The starting condition is not satisfied. | - Repair the motor or power system; - Clean out rotor part; - Clean or renew the bearing;. - Check and supply the needed condition. |
| Pump loses prime or not enough flow | - In the side of discharge or suction or impeller is clogged by impurity; - The wearing is worn out or impeller is damaged; - Rotating direction is wrong; - Speed is too low; - Low submerged height. | - Clean the strainer, impeller, diffuser, discharge pipe; - Renew the damaged parts; - Correct direction; - Measuring voltage, frequency , motor, and adjust; - Raise the suction water level. |
| Pump requires excessive power | - Bearing is damaged (include guide bearing) ; - Some impurity is in pump; - The friction between impeller and wearing 4.Packing is too tighten; - Speed is too fast; - Pump is over the operating range; - One of the electric line is short; | - Renew the bearing; - Clean these impurity; - Adjust clearance; - Loosen the packing gland; - Check voltage, frequency, motor, and adjust it; - Adjust the valve switch; - Check and repair electric line. |
| Unexpected noise are heard and Pump vibrates heavily | - Not enough submerged height, pump have cavitation; - Impeller lose balance; - Shaft is bent or shaft is not in center; - The foundation bolts is loose; - Bearing is damaged; - Frication between guide bearing and sleeve, the clearance is too big; - Discharge pipe is not reasonable; | - Increase suction water level or decrease the discharge flow; - The impeller have static balance test; - Adjust shaft; - Screw up foundation bolts; - Renew the bearing; - Renew guide bearing and shaft sleeve; - Check and clear out the pipe effect. |
| The bearing is overheated | - Unreasonable assembly, shaft is over center; - Bearing is damage; - The oil is not enough; | - Correct the co-axial degree; - Renew the bearing; - Add lubricating oil. |