S型

单级双吸水平中开式离心泵

Type S Single-stage Double-suction Horizontal

Split Centrifugal Pump

安装使用说明书

Instruction On Installation And Operation

长沙福斯水泵泵业有限公司

Fuchs Changsha Pump pump industry limited company

一、概述

S型泵为单级双吸水平中开式离心泵，适应于工厂、城市、矿山、电站、农田、水利工程等领域。用输送不含固体颗粒的清水或物理、化学性质类似于水的其它液体，被输送的介质温度为0℃～80℃。允许最大进口压力0.6Mpa。

参数范围： 流量Q   112～10800m3/h      扬程H  8.5～140m

型号说明：

如：800S24A

800——吸入口径为800mm

S——单级双吸水平中开式离心泵

24——设计点扬程为24m

A——表示叶轮外径第一次变化，A、B、C……依次类推

二、结构说明

S型泵吸入和吐出均在泵轴心线下方，与轴线垂直成水平方向。检修时将泵盖揭开即可将全部零件拆下，不必动电机及管路。

S型泵主要由泵体、泵盖、叶轮、轴、轴套、双吸密封环、轴承部分和填料密封部分组成。叶轮、密封环、轴套为易损零件。

叶轮用轴套和轴套螺母固定在轴上，其轴向位置可以通过轴套螺母进行调整，叶轮的轴向力通过其自身叶片对称布置达到平衡。

双吸密封环用以减小水泵压水室的水漏回吸水室。

泵的轴封分填料密封和机械密封两种，轴承润滑方式分干油润滑和稀油润滑两种，当泵口径为800mm以下基本采用干油润滑，泵口径为800mm以上基本采用稀油润滑。

泵通过弹性柱销联轴器与电动机联接。

旋转方向：从传动端看，泵为顺时针方向旋转，此时吸入口在右，吐出口在左。（如用户需要，亦可改为逆时针方向旋转）

主要零部件材质：泵的过流部件材质均为铸铁。（如用户需要，叶轮亦可用铸钢或黄铜铸造。

Ⅰ、General

Type S pump is single-stage double-suction centrifugal pump with horizontal split casing. It is provided for delivering clear water without solid particles or other liquid which is physically and chemically similar to clear water. The temperature of the liquid is 0℃～80℃. It is widely used in fields of factories, mines, municipal water supply. Power stations, agriculture irrigation and water conservancy. Permissible maximum inlet pressure is 0.6 MPa.

Performance range:

Capacity   Q: 112m3/h~10800 m3/h

Head      H: 8.5m~140m

The description of pump type

For example 800S24A

800-----Inlet diameter is 800mm

S-------Single-stage double-suction centrifugal pump with horizontal split casing

24------Head at design point is 24m

A-------A,B,C separately represents outer diameter of impeller has been cut the first, the second and the third time.

Ⅱ、Construction:

The inlet and the outlet of the pump are under the axis， and their centerline is perpendicular to the axis ,it is unnecessary to disturb the inlet piping , the outlet piping and the motor while inspection.

The main parts of the pump consist of casing, pump cover, impeller, shaft, shaft sleeve and double-suction wearing ring, etc. Impeller, shaft sleeve and double-suction wearing ring are consumable parts.

The impeller is fixed on the shaft with the shaft sleeves and the sleeve nuts, its axial displacement will be adjusted by the sleeve nut. The thrust of the impeller will be balanced with the help of symmetric vanes.

The double-suction wearing ting is to reduce leakage from pressure water house to suction house.

The shaft seal is either packing seal or mechanical seal. The bearing lubricated oil has dry-oil and dilute-oil; When the inlet diameter of the pump more than 800mm, the bearing get lubricated with dilute-oil.

The pump is connected with the motor through flexible coupling.

The direction of rotation

The rotation of the pump rotor is clockwise looking from the driver to the pump, i.e. the inlet is on the right and the outlet is on the left. Ii is also counter clockwise according to customers’ requirement.

The material of main parts of pump

The medium-contacting parts are made of cast iron.

三、结构图（Ⅲ Sectional Arrangement Figure）

四、安装、起动、停车和运行

安装

1、安装前的准备工作

（1）检查水泵和电机有无损坏。  （2）按图检查机组的基础。

2、安装要求

（1）泵与电机的轴心线应位于水平面内。

（2）泵与电机的轴心线应在同一直线上。

（3）使泵和电机联轴器之间留3~5毫米间隙。

（4）在泵接上管道后，应按上述要求再校正一次。

起动与停车

1、将轴及其他涂油零件上的油去净。

2、用汽油清洗轴承和油室，用棉纱或破布擦净。

3、装滚珠轴承的泵用黄油作润滑剂，注入轴承时，以占轴承体空间的70%为宜，用稀油润滑的泵，油位应在油标二刻线之间。

4、先取出联轴器的圆柱销，起动电机，检查电机旋转方向，再装好联轴器柱销。

5、经泵盖上方螺孔往泵内灌注水或用真空泵抽除空气引水。

6、闭上吐出管上的闸阀和压力表旋塞。

7、起动电机，打开压力表旋塞。

8、当水泵达到规定转速时，压力表显示相应的压力，然后打开真空气旋塞，并逐渐打开排水管道上的闸阀，调整到需要的压力为止。

- 停止水泵时，要慢慢关闭闸伐和真空计旋塞，然后停止电动机，关闭压力旋塞，若所处环境温度较低时，应将泵体最下方的旋塞打开，放出泵内余水，以免冻裂。

10、当长期停止使用水泵时，应将水泵拆开，擦干零件上的水，并在加工面上涂上防锈油，妥善保存。

运转

1、注意轴承温度，不应超过外界35℃，最高温度不应超过75℃。

2、填料室的漏水以每分钟10~20滴为正常。

3、定期检查弹性联轴器。

4、水泵运行过程中应进行周期性检查。叶轮与密封环间的间隙磨损过大时，应更换叶轮或密封环。

Ⅳ Installation, Start-up, Operation and shut-off

Installation

- Preliminaries before installation

- Inspect whether the pump and the motor are damaged.

- Examine the foundation of the machine unit according to the drawing.

- Requirements in installing

- The axes of the pump and motor must be on the same horizontal plane.

- The axes of the pump and motor must be on the same straight line.

- A certain clearance between the coupling halves of the pump and the motor should be kept in conformity to the drawing.

- Inspection should be repeated in the light of the above requirements after the pump is connected with the pipe lines.

Starting and Stopping

- Remove the grease on the shaft and other oiled parts..

- Cleanse the bearings and oil chambers with gasoline and dry them with cotton waste or rage.

- In respect to the pump with ball bearing lubricated with grease, it is suitable to fill 70% of the rooms of the bearing boxes. The oil level of the pump lubricated with thin oil should be between the two scales on the oil level indicator.

- First, take the coupling pins off; secondly, start the motor to inspect its rotation direction and lastly, put the coupling pins on..

- Fill the pump with water through the hole with screw thread in the upper part of the pump cover prime with a vacuum pump.

- Close the gate valve in the discharge line and the cock in the manometer.

- Start the motor and open the cock in the manometer.

- When the pump runs to a rated speed and the manometer shows a corresponding press-. ure , open the cock in the vacuum gauge and open gradually the gate valve in the disch- arge line until the required pressure is obtained.

- When stop the pump, close slowly the gate valve and the cock in the vacuum gauge; then stop the motor and close the cock in the manometer. If the pump stands an a freezi-

ng temperature, the screw plug in the lowest part of the pump body should be twisted to let the remaining water run out of the pump for preventing cracks due to freezing.

- If the pump is to be idle for long periods, it should be taken apart, dried ,oiled with picking oil on the polished surfaces and preserved judiciously.

Operating

- Care to keep the temperature of the bearing not being 35℃ higher than that in surroun-

Dings and itself not being over 75℃.

- It is normal that the liquid in the stuffing box leaks 10~20 drops pear minute.

- Inspect the elastic coupling periodically.

- In the operation period, the pump should be examined periodically. If the clearance between the impeller and wearing ring is to large, the former or the latter should be replaced.

五、可能发生的故障及其解决的方法

| 故障 | 原因 | 解决方法 |
| --- | --- | --- |
| 1、水泵不吸水，压力表及真空表的指针在剧烈跳动。 | 注入水泵的水不够，水管与仪表漏气。 | 再往水泵注水，拧紧或堵塞漏处。 |
| 2、水泵不吸水真空表指示高度真空。 | 底间没有打开或已污塞，吸水管阻力太大，吸水高度太大。 | 校正或更换底阀，清洗或更改吸水管，降低吸水高度。 |
| 3、看压力表水泵出水处是有压力然而水泵仍不出水。 | 出水管阻力太大，旋转方向不对，叶轮污塞，水泵转速不够。 | 检查或缩短水管及检查电机转向，清洗叶轮，增加水泵的转速。 |
| 4、流量低于预计。 | 水泵污塞或是密封环磨损过多，转速不够。 | 清洗水泵及管子，更换新的密封环，增加水泵的转速。 |
| 5、水泵消耗的功率过大。 | 填料压盖太紧，填料函发热，叶轮损坏了，水泵供水量增加。 | 拧松填料盖或将填料取出来打开一些，更换叶轮，关小闸阀以降低流量。 |
| 6、水泵内部声音反常，水泵不上水。 | 闸门开得太大，吸水管内阻力过大，吸水高度过大，在吸水处有空气渗入，所压送的液体温度过高。 | 关心闸阀以减少流量，检查泵吸水管，检查底阀，减小吸水高度，拧紧或堵塞漏气处，降低液体温度。 |
| 7、水泵振动。 | 泵轴与电机轴不在同一条中心线上。 | 把水泵和电机的轴心线对准。 |
| 8、轴承过热。 | 没有油，水泵轴与电机轴不在一条中心线上，油环不旋转。 | 加油，把轴中心线对准，检查或清洗轴承体。 |

Ⅴ Possible trouble and their remedies

| Trouble | Cause | Remedy |
| --- | --- | --- |
| 1. Pump doesn’t suck, pointers in manometer and vacuum gauge pulsate viol- ently | Water filled into pump insufficient, air leaks in pipe lines and meters. | Refill water into the pump, block leaks. |
| 2. Pump doesn’t suck, Vacuum gauge shows high vacuum | Bottom valve is not opened or blocked, resistance in suction line too large, suction head too large. | Adjust or replace bottom valve, clean or change suction line, lower suction head. |
| 3. Manometer shows press- ure, but pump delivers no water yet | Resistance in discharge line too large, rotation direction incorrect, impeller blocked, speed of rotation not enough | Inspect or shorten pipe lines and inspect motor rotation direction, clean impeller, increase speed of rotation of pump. |
| 4. Capacity lower than that expected | Pump blocked or wearing ring worn too much, speed of rotation not enough | Clean pump and pipe lines, Replace wearing ring, increase speed of rotation of pump. |
| 5. Power consumed too much | Stuffing gland too tight, stuffing box heated, impeller worn badly, amount of water supply increased. | Loosen stuffing gland or take stuffing off to be squared, replace impeller, adjust gate valve to lower capacity. |
| 6. Pump is noisy and doesn’t suck | Gate valve opened too large, resistance in suction line too large, suction head too large, suction opening, temperature of liquid delivered too high | Adjust gate valve to lower capacity, inspect suction line, inspect bottom valve, lower suction head, block leaks, lower temperature of liquid. |
| 7. Pump vibrates | Shaft centerlines of pump and motor not in alignment. | Align shaft centerline of pump with that of motor. |
| 8. Bearing over heated | No oil, shaft centerlines of pump and motor not in alignment, oil ring doesn’t run | Add oil, align the shaft centerlines, inspect or clean bearing box. |

S 型 性 能 参 数 表

The Performance Date Of Type S Pumps

| 型 号 Type | 流量 Capacity Q (m3/h) | 扬程 Head H (m) | 转速 Speed n (r/min) | 效率 Eff. η （%） | 功 率Power |  | 必需汽 蚀余量 (NPSH)r (m) | 电机型号 Motor | 泵重 Pump Weight (kg) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | 轴功率 Shaft Power (KW) | 电机功率 Motor Power (KW) |  |  |  |
| 150S50 | 108 | 58 | 2950 | 70 | 24.4 | 37 | 2.9 | Y200L2-2 | 110 |
|  | 160 | 54 |  | 81 | 29.0 |  | 3.8 |  |  |
|  | 193 | 50 |  | 84 | 31.2 |  | 4.4 |  |  |
| 150S50A | 108 | 46 | 2950 | 76 | 17.8 | 30 | 2.9 | Y200L1-2 | 110 |
|  | 144 | 44 |  | 80 | 21.5 |  | 3.8 |  |  |
|  | 174 | 39 |  | 80 | 23.1 |  | 4.4 |  |  |
| 150S50B | 108 | 38 | 2950 | 72 | 15.5 | 22 | 2.9 | Y180M-2 | 110 |
|  | 133 | 36 |  | 77 | 16.9 |  | 3.8 |  |  |
|  | 160 | 32 |  | 77 | 18.1 |  | 4.4 |  |  |
| 150S97 | 126 | 73 | 2950 | 73 | 49.9 | 75 | 3.0 | Y280S-2 | 150 |
|  | 180 | 80 |  | 80 | 59.5 |  | 3.8 |  |  |
|  | 216 | 79 |  | 79 | 64.8 |  | 5.3 |  |  |
| 150S97A | 119 | 91 | 2950 | 70 | 42.0 | 75 | 3.0 | Y280S-2 | 150 |
|  | 170 | 84.5 |  | 78 | 50.1 |  | 3.8 |  |  |
|  | 204 | 76 |  | 77 | 54.8 |  | 5.3 |  |  |
| 150S97B | 72 | 24.0 | 1480 | 73 | 6.45 | 11 | 2.6 | Y160M-4 | 150 |
|  | 90 | 22.5 |  | 74 | 7.45 |  | 2.7 |  |  |
|  | 108 | 20.0 |  | 70 | 8.40 |  | 2.9 |  |  |
| 200S95 | 216 | 99 | 2950 | 74 | 78.6 | 132 | 4.0 | Y315M-2 | 215 |
|  | 280 | 95 |  | 80 | 90.8 |  | 4.7 |  |  |
|  | 336 | 87 |  | 79 | 101.1 |  | 6.6 |  |  |
| 200S95A | 210 | 87 | 2950 | 73 | 68.1 | 110 | 4.0 | Y315S-2 | 215 |
|  | 262 | 83 |  | 77 | 76.9 |  | 4.5 |  |  |
|  | 314 | 74 |  | 76 | 83.3 |  | 5.7 |  |  |
| 200S95B | 196 | 76 | 2950 | 72 | 57.0 | 75 | 4.0 | Y280S-2 | 215 |
|  | 247 | 73 |  | 76 | 64.6 |  | 4.2 |  |  |
|  | 300 | 63 |  | 72 | 71.4 |  | 5.4 |  |  |
| 150S78 | 126 | 84 | 2980 | 72 | 40 | 55 | 5.9 | Y250M-2 | 150 |
|  | 160 | 78 |  | 75 | 45.3 |  |  |  |  |
|  | 198 | 70 |  | 74 | 51 |  |  |  |  |
| 150S78A | 112 | 67 | 2980 | 68 | 29.6 | 45 | 5.9 | Y225M-2 | 150 |
|  | 144 | 62 |  | 72 | 33.8 |  |  |  |  |
|  | 180 | 55 |  | 70 | 36.9 |  |  |  |  |
| 150S78B | 112 | 42 | 2980 | 68 | 20.5 | 37 | 5.9 | Y200L2-2 | 150 |
|  | 144 | 40 |  | 70 | 22.4 |  |  |  |  |
|  | 170 | 37 |  | 68 | 25.2 |  |  |  |  |

S 型 性 能 参 数 表

The Performance Date Of Type S Pumps

| 型 号 Type | 流量 Capacity Q (m3/h) | 扬程 Head H (m) | 转速 Speed n (r/min) | 效率 Eff. η （%） | 功 率Power |  | 必需汽 蚀余量 (NPSH)r (m) | 电机型号 Motor | 泵重 Pump Weight (kg) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | 轴功率 Shaft Power (KW) | 电机功率 Motor Power (KW) |  |  |  |
| 200S42 | 216 | 48 | 2980 | 81 | 34.9 | 55 | 5.4 | Y250M-2 | 200 |
|  | 280 | 42 |  | 85 | 37.7 |  |  |  |  |
|  | 342 | 35 |  | 81 | 40.2 |  |  |  |  |
| 200S42A | 198 | 43 | 2980 | 76 | 30.5 | 37 | 5.4 | Y200L2-2 | 200 |
|  | 270 | 36 |  | 80 | 33.1 |  |  |  |  |
|  | 310 | 31 |  | 76 | 34.4 |  |  |  |  |
| 200S63 | 216 | 69 | 2980 | 73.3 | 55.1 | 75 | 5.4 | Y280S-2 | 230 |
|  | 280 | 63 |  | 81 | 59.3 |  |  |  |  |
|  | 351 | 50 |  | 70.5 | 67.8 |  |  |  |  |
| 200S63A | 180 | 54.5 | 2980 | 65 | 41.1 | 55 | 5.4 | Y250M-2 | 230 |
|  | 270 | 46 |  | 70 | 48.3 |  |  |  |  |
|  | 324 | 37.5 |  | 65 | 50.9 |  |  |  |  |
| 250S14 | 300 | 17.5 | 1480 | 72.5 | 19.7 | 30 | 2 | Y200L-4 | 520 |
|  | 485 | 14 |  | 85.6 | 22.6 |  | 3.39 |  |  |
|  | 585 | 12 |  | 82.7 | 23.3 |  | 4.18 |  |  |
| 250S14A | 320 | 13.7 | 1480 | 78 | 15.3 | 22 | 3.2 | Y180L-4 | 520 |
|  | 430 | 11 |  | 82 | 15.7 |  |  |  |  |
|  | 504 | 8.6 |  | 75 | 15.73 |  |  |  |  |
| 250S24 | 360 | 27 | 1480 | 80 | 33.1 | 45 | 3.5 | Y225M-4 | 580 |
|  | 485 | 24 |  | 86 | 36.9 |  |  |  |  |
|  | 576 | 19 |  | 82 | 36.3 |  |  |  |  |
| 250S24A | 342 | 22.2 | 1480 | 80 | 25.8 | 37 | 3.5 | Y225S-4 | 580 |
|  | 414 | 20.3 |  | 83 | 27.6 |  |  |  |  |
|  | 482 | 17.4 |  | 80 | 28.6 |  |  |  |  |
| 250S39 | 360 | 42.5 | 1480 | 76 | 54.8 | 75 | 3.2 | Y280S-4 | 620 |
|  | 485 | 39 |  | 83 | 62.1 |  |  |  |  |
|  | 612 | 32.5 |  | 79 | 68.6 |  |  |  |  |
| 250S39A | 324 | 35.5 | 1480 | 74 | 42.3 | 55 | 3.2 | Y250M-4 | 620 |
|  | 468 | 30.5 |  | 79 | 49.2 |  |  |  |  |
|  | 576 | 25 |  | 77 | 50.9 |  |  |  |  |
| 250S65 | 360 | 71 | 1480 | 75 | 92.9 | 132 | 3 | Y315M-4 | 831 |
|  | 485 | 65 |  | 79 | 108.7 |  |  |  |  |
|  | 582 | 60 |  | 75 | 126.9 |  |  |  |  |
| 250S65A | 338 | 60 | 1480 | 74 | 74.7 | 110 | 3 | Y315S-4 | 831 |
|  | 462 | 53 |  | 77 | 86.8 |  |  |  |  |
|  | 535 | 49 |  | 75 | 95.2 |  |  |  |  |

S 型 性 能 参 数 表

The Performance Date Of Type S Pumps

| 型 号 Type | 流量 Capacity Q (m3/h) | 扬程 Head H (m) | 转速 Speed n (r/min) | 效率 Eff. η （%） | 功 率Power |  | 必需汽 蚀余量 (NPSH)r (m) | 电机型号 Motor | 泵重 Pump Weight (kg) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | 轴功率 Shaft Power (KW) | 电机功率 Motor Power (KW) |  |  |  |
| 300S12 | 612 | 13.6 | 1480 | 78 | 30.2 | 37 | 5.8 | Y225S-4 | 720 |
|  | 790 | 11.25 |  | 83 | 31.1 |  |  |  |  |
|  | 900 | 9.4 |  | 80 | 33.1 |  |  |  |  |
| 300S12A | 515 | 11.5 | 1480 | 73 | 22.1 | 30 | 5.8 | Y200L-4 | 720 |
|  | 675 | 9.7 |  | 78 | 22.9 |  |  |  |  |
|  | 781 | 8.5 |  | 76 | 23.8 |  |  |  |  |
| 300S19 | 612 | 22 | 1480 | 80 | 45.9 | 55 | 5.8 | Y250M-4 | 1200 |
|  | 790 | 19 |  | 87 | 46.9 |  |  |  |  |
|  | 935 | 14 |  | 75 | 47.6 |  |  |  |  |
| 300S19A | 485 | 18.5 | 1480 | 71 | 34.4 | 45 | 5.8 | Y225M-4 | 1200 |
|  | 693 | 14.8 |  | 80 | 34.9 |  |  |  |  |
|  | 798 | 12.1 |  | 75 | 35.1 |  |  |  |  |
| 300S32 | 612 | 38 | 1480 | 83 | 76.2 | 110 | 5.8 | Y315S-4 | 810 |
|  | 790 | 32 |  | 87 | 79 |  |  |  |  |
|  | 900 | 28 |  | 80 | 86 |  |  |  |  |
| 300S32A | 537 | 29.5 | 1480 | 80 | 53.9 | 75 | 5.8 | Y280S-4 | 810 |
|  | 702 | 24.7 |  | 84 | 56.2 |  |  |  |  |
|  | 790 | 22.8 |  | 78 | 62.9 |  |  |  |  |
| 300S58 | 576 | 65 | 1480 | 75 | 136 | 185 | 5.8 | Y315M1-4 | 943 |
|  | 790 | 58 |  | 84 | 148.5 |  |  |  |  |
|  | 972 | 50 |  | 80 | 165.5 |  |  |  |  |
| 300S58A | 529 | 147 | 1480 | 74 | 107 | 160 | 5.8 | Y315L1-4 | 943 |
|  | 720 | 200 |  | 81 | 118.6 |  |  |  |  |
|  | 893 | 248 |  | 78 | 131 |  |  |  |  |
| 300S58B | 504 | 47.2 | 1480 | 73 | 88.8 | 132 | 5.8 | Y315M-4 | 943 |
|  | 684 | 43 |  | 80 | 100 |  |  |  |  |
|  | 835 | 37 |  | 78 | 108 |  |  |  |  |
| 300S90 | 590 | 93 | 1480 | 74 | 202 | 315 | 5.8 | Y355L2-4 | 1056 |
|  | 790 | 90 |  | 80 | 242 |  |  |  |  |
|  | 936 | 82 |  | 75 | 279 |  |  |  |  |
| 300S90A | 576 | 86 | 1480 | 71 | 190 | 280 | 5.8 | Y355L1-4 | 1056 |
|  | 756 | 78 |  | 74 | 217 |  |  |  |  |
|  | 918 | 70 |  | 71 | 247 |  |  |  |  |
| 300S90B | 540 | 72 | 1480 | 70 | 151 | 220 |  | Y355M1-4 | 1056 |
|  | 720 | 67 |  | 73 | 180 |  | 5.8 |  |  |
|  | 900 | 57 |  | 70 | 200 |  |  |  |  |

S 型 性 能 参 数 表

The Performance Date Of Type S Pumps

| 型 号 Type | 流量 Capacity Q (m3/h) |  | 扬程 Head H (m) | 转速 Speed n (r/min) |  |  | 效率 Eff. η （%） | 功 率Power |  |  | 必需汽 蚀余量 (NPSH)r (m) |  |  | 电机型号 Motor | 泵重 Pump Weight (kg) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | 轴功率 Shaft Power (KW) |  | 电机功率 Motor Power (KW) |  |  |  |  |  |
| 350S16 | 972 |  | 20 | 1480 |  |  | 83 | 63.8 |  | 75 |  |  |  | Y280S-4 | 895 |
|  | 1260 |  | 16 |  |  |  | 86 | 63.9 |  |  | 5.3 |  |  |  |  |
|  | 1476 |  | 13.4 |  |  |  | 74 | 72.8 |  |  |  |  |  |  |  |
| 350S16A | 800 |  | 13.7 | 1480 |  |  | 74 | 40.3 |  | 55 |  |  |  | Y250M-4 | 895 |
|  | 967 |  | 11.5 |  |  |  | 78 | 38.8 |  |  | 5.3 |  |  |  |  |
|  | 1167 |  | 8.6 |  |  |  | 70 | 39 |  |  |  |  |  |  |  |
| 350S26 | 972 |  | 32 | 1480 |  |  | 85 | 99.7 |  | 132 | 4.46 |  |  | Y315M-4 | 875 |
|  | 1260 |  | 26 |  |  |  | 88 | 101.5 |  |  | 4.75 |  |  |  |  |
|  | 1440 |  | 22 |  |  |  | 82 | 105 |  |  | 5.63 |  |  |  |  |
| 350S26A | 843 |  | 24.7 | 1480 |  |  | 80 | 70.9 |  | 90 | 6.7 |  |  | Y280M-4 | 875 |
|  | 1088 |  | 20.4 |  |  |  | 83 | 72.8 |  |  |  |  |  |  |  |
|  | 1264 |  | 15.7 |  |  |  | 73 | 74 |  |  |  |  |  |  |  |
| 350S44 |  | 972 | 50 |  | 1480 | 81 |  | 164 | 220 |  |  | 3.08 | Y355M1-4 |  | 1120 |
|  |  | 1260 | 44 |  |  | 87 |  | 177.6 |  |  |  | 4.4 |  |  |  |
|  |  | 1476 | 37 |  |  | 79 |  | 189 |  |  |  | 6.0 |  |  |  |
| 350S44A |  | 876 | 42 |  | 1480 | 80 |  | 125.2 | 160 |  |  | 5.3 | Y315L1-4 |  | 1120 |
|  |  | 1131 | 37 |  |  | 84 |  | 135.8 |  |  |  |  |  |  |  |
|  |  | 1350 | 31 |  |  | 80 |  | 142.6 |  |  |  |  |  |  |  |
| 350S75 |  | 972 | 80 |  | 1480 | 78 |  | 271 | 355 |  |  | 5.3 | Y4501-4 |  | 1200 |
|  |  | 1260 | 75 |  |  | 85 |  | 303 |  |  |  |  |  |  |  |
|  |  | 1440 | 65 |  |  | 80 |  | 319 |  |  |  |  |  |  |  |
| 350S75A |  | 900 | 70 |  | 1480 | 78 |  | 220 | 280 |  |  | 5.3 | Y355L1-4 |  | 1200 |
|  |  | 1170 | 65 |  |  | 84 |  | 247 |  |  |  |  |  |  |  |
|  |  | 1332 | 56 |  |  | 79 |  | 257 |  |  |  |  |  |  |  |
| 350S75B |  | 813 | 57 |  | 1480 | 75 |  | 168 | 220 |  |  | 5.3 | Y355M1-4 |  | 1200 |
|  |  | 1060 | 53 |  |  | 82 |  | 187 |  |  |  |  |  |  |  |
|  |  | 1202 | 45.8 |  |  | 77 |  | 195 |  |  |  |  |  |  |  |
| 350S125 |  | 850 | 140 |  | 1480 | 70 |  | 463 | 710 |  |  | 5.3 | Y5001-4 |  | 1420 |
|  |  | 1260 | 125 |  |  | 81 |  | 530 |  |  |  |  |  |  |  |
|  |  | 1660 | 100 |  |  | 72.5 |  | 624 |  |  |  |  |  |  |  |
| 350S125A |  | 787 | 120 |  | 1480 | 70 |  | 367 | 560 |  |  | 5.3 | Y4505-4 |  | 1420 |
|  |  | 1157 | 107 |  |  | 78 |  | 432 |  |  |  |  |  |  |  |
|  |  | 1538 | 86 |  |  | 70 |  | 515 |  |  |  |  |  |  |  |
| 350S125B |  | 754 | 108 |  | 1480 | 70 |  | 313 | 500 |  |  | 5.3 | Y4504-4 |  | 1420 |
|  |  | 1098 | 96 |  |  | 77 |  | 373 |  |  |  |  |  |  |  |
|  |  | 1448 | 77 |  |  | 72.5 |  | 419 |  |  |  |  |  |  |  |

S 型 性 能 参 数 表

The Performance Date Of Type S Pumps

| 型 号 Type | 流量 Capacity Q (m3/h) | 扬程 Head H (m) | 转速 Speed n (r/min) | 效率 Eff. η （%） | 功 率Power |  | 必需汽 蚀余量 (NPSH)r (m) | 电机 型号 Motor | 泵重 Pump Weight (kg) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | 轴功率 Shaft Power (KW) | 电机功率 Motor Power (KW) |  |  |  |
| 500S13 | 1620 | 15 | 980 | 79 | 83.8 | 110 | 4.5 | Y315L1-6 | 2173 |
|  | 2020 | 13 |  | 83 | 86.2 |  | 4.7 |  |  |
|  | 2340 | 10.4 |  | 80 | 82.8 |  | 5.0 |  |  |
| 500S13A | 1490 | 12.8 | 980 | 77.8 | 66.8 | 75 | 4.5 | Y315S-6 | 2173 |
|  | 1860 | 11 |  | 82 | 68 |  | 4.7 |  |  |
|  | 2100 | 9 |  | 78.6 | 65.5 |  | 5.0 |  |  |
| 500S22 | 1620 | 24.5 | 980 | 77 | 140.4 | 185 | 5.2 | Y355M2-6 | 1680 |
|  | 2020 | 22 |  | 84 | 144.1 |  |  |  |  |
|  | 2340 | 19.4 |  | 85 | 145.4 |  |  |  |  |
| 500S22A | 1400 | 20 | 980 | 74 | 103 | 132 | 5.2 | Y315L2-6 | 1680 |
|  | 1746 | 17 |  | 80 | 101 |  |  |  |  |
|  | 2020 | 14 |  | 82.1 | 93.8 |  |  |  |  |
| 500S35 | 1620 | 40 | 980 | 85 | 207.6 | 250 | 4.8 | Y450-6* | 2340 |
|  | 2020 | 35 |  | 88 | 219 |  |  |  |  |
|  | 2340 | 28 |  | 85 | 210 |  |  |  |  |
| 500S35A | 1400 | 31 | 980 | 82 | 144 | 220 | 4.8 | Y355L1-6 | 2340 |
|  | 1746 | 27 |  | 85 | 151 |  |  |  |  |
|  | 2020 | 21 |  | 84 | 138 |  |  |  |  |
| 500S40 | 1788 | 42.5 | 980 | 88.2 | 234.8 | 280 | 3 | Y4002-6 | 2400 |
|  | 2020 | 40.3 |  | 90.5 | 245.1 |  | 3.2 |  |  |
|  | 2314 | 36.4 |  | 91.1 | 251.9 |  | 4.1 |  |  |
| 500S44A | 1676 | 37.9 | 980 | 87.1 | 198.7 | 250 | 3 | Y3556-6 | 2400 |
|  | 1969 | 35 |  | 89 | 211 |  | 3.2 |  |  |
|  | 2262 | 31.2 |  | 86 | 223.6 |  | 4.1 |  |  |
| 500S59 | 1620 | 68 | 980 | 79 | 380 | 450 | 4.5 | Y4506-6 | 2747 |
|  | 2020 | 59 |  | 83 | 391 |  |  |  |  |
|  | 2340 | 47 |  | 80 | 374 |  |  |  |  |
| 500S59A | 1500 | 57 | 980 | 74 | 315 | 400 | 4.5 | Y4505-6 | 2747 |
|  | 1872 | 49 |  | 75 | 330 |  |  |  |  |
|  | 2170 | 39 |  | 72 | 320 |  |  |  |  |
| 500S59B | 1400 | 46 | 980 | 73 | 240 | 315 | 4.5 | Y4503-6 | 2747 |
|  | 1746 | 40 |  | 74 | 257 |  |  |  |  |
|  | 2020 | 32 |  | 71 | 248 |  |  |  |  |
| 500S98 | 1620 | 114 | 980 | 78 | 644.8 | 800 | 4 | Y5005-6 | 3800 |
|  | 2020 | 98 |  | 79.4 | 678 |  |  |  |  |
|  | 2340 | 79 |  | 74 | 680.3 |  |  |  |  |

S 型 性 能 参 数 表

The Performance Date Of Type S Pumps

| 型 号 Type | 流量 Capacity Q (m3/h) | 扬程 Head H (m) | 转速 Speed n (r/min) | 效率 Eff. η （%） | 功 率Power |  | 必需汽 蚀余量 (NPSH)r (m) | 电机 型号 Motor | 泵重 Pump Weight (kg) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | 轴功率 Shaft Power (KW) | 电机功率 Motor Power (KW) |  |  |  |
| 500S98A | 1500 | 96 | 980 | 77 | 509.3 | 630 | 4 | Y5003-6 | 3800 |
|  | 1872 | 83 |  | 78.5 | 540 |  |  |  |  |
|  | 2170 | 67 |  | 73 | 542.4 |  |  |  |  |
| 500S98B | 1400 | 86 | 980 | 76 | 431.4 | 560 | 4 | Y5002-6 | 3800 |
|  | 1746 | 74 |  | 78 | 452 |  |  |  |  |
|  | 2020 | 59 |  | 75 | 432.8 |  |  |  |  |
| 600S22 | 2593 | 27.6 | 980 | 86 | 226.8 | 280 | 7 | Y450-6* | 2200 |
|  | 3241 | 23.1 |  | 88 | 231.8 |  |  |  |  |
|  | 3739 | 18 |  | 79 | 232.1 |  |  |  |  |
| 600S22A | 2288 | 21.5 | 980 | 85 | 157.5 | 185 | 7 | Y355M-6 | 2200 |
|  | 2860 | 18 |  | 87 | 161 |  |  |  |  |
|  | 3300 | 14 |  | 78 | 161.2 |  |  |  |  |
| 600S32 | 2700 | 33.5 | 980 | 85 | 291.7 | 400 | 6.4 | Y4505-6 | 3149 |
|  | 3240 | 32 |  | 89 | 317.5 |  |  |  |  |
|  | 3600 | 26 |  | 84 | 298 |  |  |  |  |
| 600S32A | 2520 | 25.5 | 980 | 85 | 205.8 | 250 | 6.4 | Y450-6* | 3149 |
|  | 3000 | 23 |  | 89 | 211 |  |  |  |  |
|  | 3165 | 19.2 |  | 84 | 196.9 |  |  |  |  |
| 600S36 | 3300 | 40 | 980 | 87 | 413.4 | 500 | 8.2 | Y5001-6 | 2400 |
|  | 3800 | 36 |  | 88 | 423.6 |  | 8.4 |  |  |
|  | 4300 | 31 |  | 85 | 427.3 |  | 8.8 |  |  |
| 600S47 | 2600 | 56.5 | 980 | 80 | 415.4 | 560 | 5.5 | Y5002-6 | 4364 |
|  | 3170 | 47 |  | 88 | 455.9 |  | 6.5 |  |  |
|  | 3600 | 40.5 |  | 86 | 461.7 |  | 8 |  |  |
| 600S47A | 2400 | 45 | 980 | 83.5 | 352.5 | 450 | 5.5 | Y4506-6 | 4364 |
|  | 2920 | 42 |  | 88 | 380 |  | 6.5 |  |  |
|  | 3500 | 35 |  | 83 | 402.2 |  | 8 |  |  |
| 600S75 | 2592 | 78 | 980 | 87 | 644.3 | 900 | 5.6 | Y5601-6 | 4350 |
|  | 3060 | 75 |  | 88 | 694.4 |  | 5.6 |  |  |
|  | 3600 | 69 |  | 80 | 760 |  | 10.1 |  |  |
| 600S75A | 2338 | 63.5 | 980 | 85.5 | 467 | 630 | 4.6 | Y5003-6 | 4350 |
|  | 3084 | 57.8 |  | 90 | 539.7 |  | 7.3 |  |  |
|  | 3248 | 56.2 |  | 89 | 552 |  | 8.2 |  |  |
| 700S40 | 3040 | 45.2 | 742 | 84.5 | 443.1 | 560 | 3.3 | Y5006-8 | 6450 |
|  | 3800 | 41.9 |  | 89.4 | 485 |  | 3.6 |  |  |
|  | 4340 | 37.7 |  | 89 | 501 |  | 5.0 |  |  |

S 型 性 能 参 数 表

The Performance Date Of Type S Pumps

| 型 号 Type | 流量 Capacity Q (m3/h) | 扬程 Head H (m) | 转速 Speed n (r/min) | 效率 Eff. η （%） | 功 率Power |  | 必需汽 蚀余量 (NPSH)r (m) | 电机 型号 Motor | 泵重 Pump Weight (kg) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | 轴功率 Shaft Power (KW) | 电机功率 Motor Power (KW) |  |  |  |
| 700S40A | 2837 | 39.6 | 742 | 83.1 | 368.4 | 500 | 3.3 | Y5005-8 | 6450 |
|  | 3800 | 34.7 |  | 88.6 | 405.6 |  | 3.6 |  |  |
|  | 4583 | 27.7 |  | 88.9 | 412.3 |  | 5.0 |  |  |
| 700S90 | 4000 | 97 | 980 | 88 | 1201 | 1600 | 5.8 | Y6302-6 | 6000 |
|  | 4700 | 90 |  | 90 | 1281 |  | 7.4 |  |  |
|  | 5500 | 77 |  | 85 | 1358 |  | 9.5 |  |  |
| 700S90J | 3000 | 56 | 742 | 86 | 532 | 630 | 3.6 | Y5601-8 | 6000 |
|  | 3600 | 52 |  | 88 | 579 |  | 4.6 |  |  |
|  | 4200 | 44 |  | 83 | 590 |  | 5.9 |  |  |
| 800S22 | 4320 | 25 | 742 | 82 | 358.7 | 450 | 7.0 | Y5004-8 | 7581 |
|  | 5500 | 22 |  | 89 | 370.2 |  |  |  |  |
|  | 6840 | 19 |  | 86 | 285.4 |  |  |  |  |
| 800S22J | 3000 | 16 | 590 | 80 | 163.4 | 250 | 5.0 | Y500-10* | 7580 |
|  | 4400 | 14 |  | 88 | 190.6 |  |  |  |  |
|  | 5040 | 12.5 |  | 85 | 201.8 |  |  |  |  |
| 800S22A | 3960 | 19 | 742 | 83 | 246.9 | 315 | 7.0 | Y5001-8 | 7580 |
|  | 4830 | 17 |  | 88 | 254.1 |  |  |  |  |
|  | 5500 | 15 |  | 86 | 261.2 |  |  |  |  |
| 800S22JA | 2800 | 13 | 590 | 80 | 123.9 | 185 | 5.0 | Y355L-10 | 7580 |
|  | 3870 | 11 |  | 87 | 133.3 |  |  |  |  |
|  | 4500 | 9.5 |  | 84 | 138.6 |  |  |  |  |
| 800S24 | 5250 | 27.5 | 742 | 82 | 479 | 630 | 9 | Y5601-8 | 5950 |
|  | 7000 | 24 |  | 90 | 506 |  |  |  |  |
|  | 8400 | 20 |  | 86 | 532 |  |  |  |  |
| 800S24J | 4170 | 17.4 | 590 | 81 | 244 | 315 | 6 | Y5004-10 | 5950 |
|  | 5600 | 15 |  | 88 | 260 |  |  |  |  |
|  | 6700 | 12.5 |  | 84 | 272 |  |  |  |  |
| 800S24A | 4840 | 23.6 | 742 | 81.5 | 382 | 500 | 9 | Y5005-8 | 5950 |
|  | 6250 | 21 |  | 88 | 406 |  |  |  |  |
|  | 7740 | 17.2 |  | 84.5 | 429 |  |  |  |  |
| 800S24JA | 3850 | 15 | 590 | 81 | 194 | 280 | 6 | Y5003-10 | 5950 |
|  | 5000 | 13 |  | 87 | 203 |  |  |  |  |
|  | 6150 | 11 |  | 84 | 219 |  |  |  |  |
| 800S32 | 4320 | 35 | 742 | 82 | 502.2 | 630 | 7 | Y5601-8 | 7600 |
|  | 5500 | 32 |  | 89 | 538.5 |  |  |  |  |
|  | 6480 | 29 |  | 87 | 588.2 |  |  |  |  |

S 型 性 能 参 数 表

The Performance Date Of Type S Pumps

| 型 号 Type | 流量 Capacity Q (m3/h) | 扬程 Head H (m) | 转速 Speed n (r/min) | 效率 Eff. η （%） | 功 率Power |  |  | 必需汽 蚀余量 (NPSH)r (m) | 电机型号 Motor | 泵重 Pump Weight (kg) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | 轴功率 Shaft Power (KW) |  | 电机功率 Motor Power (KW) |  |  |  |
| 800S32A | 3500 | 30 | 742 | 81 | 353 |  | 450 | 7 | Y5004-8 | 7600 |
|  | 4950 | 26 |  | 88 | 398.3 |  |  |  |  |  |
|  | 6000 | 23 |  | 86 | 437 |  |  |  |  |  |
| 800S47 | 4320 | 51 | 742 | 81 | 740.7 |  | 1000 | 6.5 | Y6301-8 | 8200 |
|  | 5500 | 47 |  | 90 | 782.2 |  |  |  |  |  |
|  | 6480 | 42 |  | 88 | 842.2 |  |  |  |  |  |
| 800S47J | 3000 | 35 | 590 | 80 | 357.4 |  | 450 | 4 | Y5601-10 | 8200 |
|  | 4400 | 33 |  | 89 | 403.9 |  |  |  |  |  |
|  | 5200 | 26 |  | 86 | 428.1 |  |  |  |  |  |
| 800S47A | 3500 | 45 | 742 | 81 | 529.5 |  | 710 | 6.5 | Y5602-8 | 8200 |
|  | 5070 | 40 |  | 89 | 620.5 |  |  |  |  |  |
|  | 6000 | 36 |  | 86 | 684 |  |  |  |  |  |
| 800S47JA | 2800 | 30 | 590 | 80 | 286 |  | 355 | 4 | Y5005-10 | 8200 |
|  | 4060 | 25 |  | 88 | 314.1 |  |  |  |  |  |
|  | 4800 | 22 |  | 86 | 334.4 |  |  |  |  |  |
| 800S76 | 5920 | 76 | 742 | 86 | 1426 |  | 1800 | 5.8 | Y710-7-8 | 9000 |
|  | 7360 | 72 |  | 92 | 1570 |  |  | 6.4 |  |  |
|  | 8075 | 69 |  | 89 | 1760 |  |  | 8.5 |  |  |
| 800S76J | 4750 | 48 | 590 | 84.7 |  | 734 | 1000 | 3.6 | Y6303-10 | 9000 |
|  | 5890 | 45.5 |  | 90.5 |  | 807 |  | 4.5 |  |  |
|  | 6365 | 43.5 |  | 88 |  | 857 |  | 5.3 |  |  |
| 800S76A | 4750 | 61 | 742 | 85 |  | 929 | 1250 | 5.8 | Y6303-8 | 9000 |
|  | 6080 | 58 |  | 91 |  | 1056 |  | 6.4 |  |  |
|  | 6745 | 55 |  | 87 |  | 1162 |  | 8.5 |  |  |
| 800S76JA | 3895 | 38.5 | 590 | 83.7 |  | 488 | 710 | 3.6 | Y5605-10 | 9000 |
|  | 4980 | 36.5 |  | 89.6 |  | 553 |  | 4.5 |  |  |
|  | 5510 | 34.8 |  | 85.7 |  | 610 |  | 5.3 |  |  |
| 800S76B | 4370 | 55 | 742 | 84.3 |  | 777 | 1120 | 5.8 | Y6302-8 | 9000 |
|  | 5550 | 52.3 |  | 90.3 |  | 876 |  | 6.4 |  |  |
|  | 6175 | 49.5 |  | 86.3 |  | 965 |  | 8.5 |  |  |
| 800S76JB | 3560 | 34.7 | 590 | 83 |  | 406 | 560 | 3.6 | Y5603-10 | 9000 |
|  | 4410 | 33 |  | 88.5 |  | 448 |  | 4.5 |  |  |
|  | 4900 | 31.3 |  | 86 |  | 486 |  | 5.3 |  |  |
| 800S76JJ | 3990 | 33.7 | 495 | 83 |  | 441 | 630 | 3.2 | Y6302-12 | 9000 |
|  | 4940 | 32 |  | 88 |  | 490 |  | 3.4 |  |  |
|  | 5320 | 30.7 |  | 84 |  | 530 |  | 3.7 |  |  |

S 型 性 能 参 数 表

The Performance Date Of Type S Pumps

| 型 号 Type |  | 流量 Capacity Q (m3/h) | 扬程 Head H (m) |  | 转速 Speed n (r/min) |  | 效率 Eff. η （%） |  | 功 率Power |  |  | 必需汽 蚀余量 (NPSH)r (m) | 电机型号 Motor | 泵重 Pump Weight (kg) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  | 轴功率 Shaft Power (KW) |  | 电机功率 Motor Power (KW) |  |  |  |  |
| 900S36 |  | 6000 | 40 |  | 590 |  | 85 |  | 769.4 |  | 1000 | 5.3 | Y6303-10 | 11200 |  |
|  |  | 7500 | 36 |  |  |  | 90 |  | 817.5 |  |  | 6.2 |  |  |  |
|  |  | 9000 | 32 |  |  |  | 86.5 |  | 907.3 |  |  | 7.3 |  |  |  |
| 900S36A |  | 5700 | 34.3 |  | 590 |  | 85.6 |  | 622.4 |  | 800 | 4 | Y6301-10 | 11200 |  |
|  |  | 6600 | 32 |  |  |  | 88 |  | 654 |  |  | 4.5 |  |  |  |
|  |  | 7900 | 27.5 |  |  |  | 86.1 |  | 687.6 |  |  | 5.3 |  |  |  |
| 900S36* |  | 7080 | 38 |  | 590 |  | 87 |  | 843 |  | 1000 | 4.7 | Y6303-10 | 11200 |  |
|  |  | 8140 | 36 |  |  |  | 89 |  | 897 |  |  | 5.1 |  |  |  |
|  |  | 9330 | 31 |  |  |  | 85 |  | 927 |  |  | 6.3 |  |  |  |
| 1200S22 |  | 7920 | 25.5 |  | 495 |  | 85.5 |  | 644 |  | 800 | 5.8 | Y6304-12 | 25600 |  |
|  |  | 9612 | 22 |  |  |  | 87 |  | 662 |  |  |  |  |  |  |
|  |  | 10800 | 18 |  |  |  | 83 |  | 638 |  |  |  |  |  |  |
| 1200S22A | 7200 |  | 22.5 | 495 |  | 83.8 |  | 534 |  | 710 |  | 5.8 | Y6303-12 | 25600 |  |
|  | 9000 |  | 20.2 |  |  | 86.5 |  | 573 |  |  |  |  |  |  |  |
|  | 10080 |  | 17.5 |  |  | 82.2 |  | 585 |  |  |  |  |  |  |  |
| 1200S32 | 8640 |  | 35 | 590 |  | 83 |  | 992 |  | 1400 |  | 7.7 | Y6304-10 |  |  |
|  | 10800 |  | 32 |  |  | 87 |  | 1082 |  |  |  |  |  |  |  |
|  | 12960 |  | 26 |  |  | 85.5 |  | 1073 |  |  |  |  |  |  |  |
| 1200S32A | 7776 |  | 32.5 | 590 |  | 82.5 |  | 834 |  | 1250 |  | 7.7 | Y6303-10 |  |  |
|  | 9720 |  | 29 |  |  | 86.5 |  | 887.5 |  |  |  |  |  |  |  |
|  | 11664 |  | 23 |  |  | 85 |  | 860 |  |  |  |  |  |  |  |
| 1200S39 | 7200 |  | 42.5 | 495 |  | 81.5 |  | 1023 |  | 1600 |  | 5.5 | Y800-1-12 |  |  |
|  | 9000 |  | 39 |  |  | 87.5 |  | 1092.4 |  |  |  |  |  |  |  |
|  | 10800 |  | 33 |  |  | 84 |  | 1155 |  |  |  |  |  |  |  |
| 1200S39A | 6480 |  | 38.5 | 495 |  | 80 |  | 849 |  | 12500 |  | 5.5 | Y710-2-12 |  |  |
|  | 8100 |  | 35 |  |  | 86.5 |  | 892.5 |  |  |  |  |  |  |  |
|  | 9720 |  | 29 |  |  | 83 |  | 925 |  |  |  |  |  |  |  |
| 1200S39B | 5832 |  | 34 | 495 |  | 80 |  | 675 |  | 1000 |  | 5.5 | Y6304-12 |  |  |
|  | 7290 |  | 31 |  |  | 85.7 |  | 718 |  |  |  |  |  |  |  |
|  | 8748 |  | 25.5 |  |  | 82 |  | 741 |  |  |  |  |  |  |  |
| 1200S56 | 8640 |  | 60.5 | 590 |  | 82 |  | 1736 |  | 2240 |  | 7.5 | Y800-1-10 |  |  |
|  | 10800 |  | 56 |  |  | 88 |  | 1871 |  |  |  |  |  |  |  |
|  | 12960 |  | 47.5 |  |  | 85.5 |  | 1960 |  |  |  |  |  |  |  |
| 1200S56A | 7776 |  | 54.5 | 590 |  | 81 |  | 1425 |  | 2000 |  | 7.5 | Y710-3-10 |  |  |
|  | 9720 |  | 50 |  |  | 87.5 |  | 1512.6 |  |  |  |  |  |  |  |
|  | 11664 |  | 42 |  |  | 83.5 |  | 1597 |  |  |  |  |  |  |  |

S 型 性 能 参 数 表

The Performance Date Of Type S Pumps

| 型 号 Type | 流量 Capacity Q (m3/h) | 扬程 Head H (m) | 转速 Speed n (r/min) | 效率 Eff. η （%） | 功 率Power |  | 必需汽 蚀余量 (NPSH)r (m) | 电机型号 Motor | 泵重 Pump Weight (kg) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | 轴功率 Shaft Power (KW) | 电机功率 Motor Power (KW) |  |  |  |
| 1200S65B | 6998.4 | 49 | 590 | 80 | 1167 | 1600 | 7.5 | Y710-1-10 |  |
|  | 8748 | 44 |  | 86 | 1218.9 |  |  |  |  |
|  | 10497 | 36.6 |  | 81.5 | 1280 |  |  |  |  |
| 1200S72 | 12240 | 64 | 742 | 88 | 2424 | 2500 | 11.7 | Y800-2-10 |  |
|  | 10224 | 72 |  | 89 | 2251 |  |  |  |  |
|  | 9000 | 74.5 |  | 86 | 2123 |  |  |  |  |

注：带*号表示叶轮模型不同（以下同）

S 型泵外形尺寸图

# The Overall Dimensions

S型泵外形尺寸表（1）

The Chart Of Overall Dimensions                                单位：mm

| 泵型号. Type | L | L1 | L2 | L3 | B | B1 | B2 | B3 | H | H1 | H2 | H3 | H4 | 4-φd | 进 水 口 法 兰Inlet Flange |  |  |  |  | 出 水 口 法 兰 Outlet Flange |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Dg1 | D01 | D1 | b1 | n-φd1 | Dg2 | D02 | D2 | b2 | n-φd2 |
| 150S50 | 628 | 337 | 250 | 200 | 450 | 200 | 300 | 220 | 445 | 270 | 20 | 135 | 140 | 4-φ18 | 150 | 225 | 260 | 20 | 8-φ17.5 | 100 | 170 | 205 | 18 | 4-φ17.5 |
| 150S97 | 696 | 375 | 320 | 270 | 550 | 250 | 300 | 240 | 500 | 290 | 25 | 130 | 172 | 4-φ24 | 150 | 225 | 265 | 20 | 8-φ17.5 | 100 | 180 | 220 | 24 | 8-φ17.5 |
| 200S95 | 784 | 421 | 320 | 270 | 650 | 300 | 340 | 280 | 566 | 340 | 25 | 170 | 185 | 4-φ23 | 200 | 280 | 320 | 22 | 8-φ17.5 | 125 | 210 | 250 | 26 | 8-φ17.5 |
| 150S78 | 727 | 410 | 300 | 250 | 550 | 250 | 340 | 250 | 472 | 285 | 25 | 140 | 155 | 4-φ18 | 150 | 240 | 285 | 24 | 8-φ22 | 100 | 180 | 220 | 22 | 8-φ17.5 |
| 200S63 | 756 | 422 | 300 | 250 | 620 | 300 | 340 | 250 | 549 | 355 | 30 | 170 | 170 | 4-φ18 | 200 | 295 | 340 | 26 | 8-φ22 | 150 | 240 | 285 | 30 | 8-φ22 |
| 200S42 | 756 | 422 | 300 | 250 | 620 | 300 | 340 | 250 | 547 | 355 | 25 | 170 | 170 | 4-φ18 | 200 | 295 | 340 | 26 | 8-φ22 | 150 | 240 | 285 | 26 | 8-φ22 |
| 250S65 | 1058 | 593 | 410 | 350 | 880 | 400 | 510 | 400 | 796 | 450 | 30 | 240 | 290 | 4-φ28 | 250 | 350 | 395 | 28 | 12-φ22 | 150 | 240 | 285 | 26 | 8-φ22 |
| 250S39 | 957.5 | 524 | 410 | 350 | 890 | 440 | 520 | 400 | 745 | 450 | 30 | 200 | 260 | 4-φ28 | 250 | 350 | 395 | 35 | 12-φ24 | 200 | 295 | 340 | 35 | 8-φ24 |
| 250S24 | 965 | 544 | 410 | 350 | 850 | 400 | 510 | 400 | 738 | 450 | 30 | 230 | 230 | 4-φ28 | 250 | 335 | 375 | 30 | 12-φ17.5 | 200 | 280 | 320 | 30 | 8-φ17.5 |
| 250S14 | 877.5 | 470 | 410 | 350 | 745 | 330 | 510 | 400 | 709 | 450 | 30 | 210 | 215 | 4-φ28 | 250 | 350 | 395 | 36 | 12-φ24 | 200 | 295 | 340 | 36 | 8-φ24 |
| 300S90 | 1200 | 676 | 520 | 450 | 1046 | 470 | 600 | 450 | 898 | 510 | 40 | 268 | 325 | 4-φ28 | 300 | 400 | 445 | 28 | 12-φ22 | 200 | 295 | 340 | 26 | 8-φ22 |
| 300S58 | 1112 | 617 | 520 | 450 | 1070 | 530 | 600 | 450 | 830 | 510 | 40 | 250 | 310 | 4-φ28 | 300 | 400 | 445 | 28 | 12-φ22 | 250 | 350 | 395 | 28 | 12-φ22 |
| 300S32 | 1102.5 | 614 | 520 | 450 | 880 | 410 | 600 | 450 | 824 | 510 | 40 | 260 | 270 | 4-φ28 | 300 | 400 | 445 | 28 | 12-φ22 | 250 | 350 | 395 | 28 | 12-φ22 |
| 300S19 | 1002.5 | 561 | 520 | 450 | 900 | 400 | 600 | 450 | 803 | 510 | 40 | 250 | 260 | 4-φ28 | 300 | 400 | 445 | 28 | 12-φ22 | 250 | 350 | 395 | 35 | 12-φ22 |
| 300S12 | 1030 | 574 | 520 | 450 | 1000 | 500 | 600 | 450 | 808 | 510 | 40 | 265 | 265 | 4-φ28 | 300 | 395 | 440 | 24 | 12-φ22 | 300 | 395 | 440 | 24 | 12-φ22 |
| 350S125 | 1403.5 | 781 | 600 | 500 | 1210 | 550 | 690 | 500 | 1080 | 620 | 50 | 330 | 410 | 4-φ35 | 350 | 460 | 505 | 30 | 16-φ22 | 200 | 295 | 340 | 26 | 12-φ22 |
| 350S75 | 1273 | 712 | 600 | 500 | 1250 | 600 | 690 | 500 | 1017 | 620 | 50 | 274 | 356 | 4-φ35 | 350 | 460 | 505 | 30 | 16-φ22 | 250 | 350 | 395 | 28 | 12-φ22 |
| 350S44 | 1264 | 707 | 600 | 500 | 1080 | 510 | 690 | 500 | 980 | 620 | 50 | 300 | 300 | 4-φ35 | 350 | 460 | 505 | 30 | 16-φ22 | 300 | 400 | 445 | 28 | 12-φ22 |
| 350S26 | 1173 | 645 | 600 | 500 | 1040 | 460 | 690 | 500 | 963 | 620 | 50 | 290 | 300 | 4-φ35 | 350 | 460 | 505 | 30 | 16-φ22 | 300 | 400 | 445 | 28 | 12-φ22 |
| 350S16 | 1132.5 | 626 | 600 | 500 | 1168 | 584 | 690 | 500 | 970 | 620 | 50 | 310 | 310 | 4-φ35 | 350 | 460 | 505 | 30 | 16-φ22 | 350 | 460 | 505 | 30 | 16-φ22 |

S型泵外形尺寸表（2）

The Chart Of Overall Dimensions                                单位：mm

| 泵型号 Type | L | L1 | L2 | L3 | B | B1 | B2 | B3 | H | H1 | H2 | H3 | H4 | 4-φd | 进 水 口 法 兰 Inlet Flange |  |  |  |  | 出 水 口 法 兰 Outlet Flange |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Dg1 | D01 | D1 | b1 | n-φd1 | Dg2 | D02 | D2 | b2 | n-φd2 |
| 500S13 | 1311.5 | 717.5 | 760 | 580 | 1550 | 775 | 1020 | 800 | 1251 | 800 | 55 | 410 | 410 | 4-φ42 | 500 | 620 | 670 | 34 | 20-φ26 | 500 | 620 | 670 | 34 | 20-φ26 |
| 500S22 | 1375.5 | 750 | 760 | 580 | 1460 | 640 | 1020 | 800 | 1266 | 800 | 55 | 410 | 410 | 4-φ42 | 500 | 620 | 670 | 34 | 20-φ26 | 400 | 515 | 565 | 32 | 16-φ26 |
| 500S35 | 1375 | 766 | 760 | 580 | 1350 | 630 | 1020 | 800 | 1270 | 800 | 55 | 415 | 415 | 4-φ42 | 500 | 620 | 670 | 34 | 20-φ26 | 350 | 460 | 505 | 30 | 16-φ22 |
| 500S59 | 1637.5 | 905 | 760 | 580 | 1640 | 810 | 1020 | 800 | 1300 | 800 | 55 | 370 | 480 | 4-φ42 | 500 | 620 | 670 | 34 | 20-φ26 | 350 | 460 | 505 | 30 | 16-φ22 |
| 500S98 | 1639.5 | 912 | 760 | 580 | 1550 | 750 | 1020 | 800 | 1381 | 800 | 55 | 425 | 545 | 4-φ42 | 500 | 620 | 670 | 34 | 20-φ26 | 300 | 400 | 445 | 34 | 12-φ22 |
| 600S22 | 1473 | 812 | 940 | 760 | 1790 | 840 | 1020 | 800 | 1476 | 950 | 55 | 460 | 460 | 4-φ41 | 600 | 725 | 780 | 36 | 20-φ30 | 500 | 620 | 670 | 34 | 20-φ25 |
| 600S32 | 2180 | 1143 | 940 | 780 | 1760 | 740 | 960 | 720 | 1480 | 900 | 60 | 550 | 525 | 4-φ36 | 600 | 725 | 780 | 44 | 20-φ30 | 500 | 620 | 670 | 44 | 20-φ25 |
| 600S47 | 1942.5 | 1085 | 1100 | 900 | 1800 | 800 | 1300 | 1000 | 1550 | 950 | 55 | 532 | 663 | 4-φ42 | 600 | 725 | 780 | 36 | 20-φ30 | 400 | 515 | 565 | 32 | 16-φ26 |
| 600S75 | 1686 | 934 | 940 | 760 | 1900 | 940 | 1020 | 800 | 1550 | 950 | 55 | 425 | 550 | 4-φ42 | 600 | 725 | 780 | 32 | 20-φ30 | 400 | 515 | 565 | 36 | 16-φ30 |
| 800S22 | 2100 | 1220 | 1200 | 1000 | 2100 | 750 | 1200 | 1000 | 2014 | 1200 | 60 | 720 | 720 | 4-φ42 | 800 | 950 | 1015 | 44 | 24-φ33 | 600 | 725 | 780 | 44 | 20-φ30 |
| 800S32 | 2100 | 1220 | 1200 | 1000 | 2100 | 750 | 1200 | 1000 | 2014 | 1200 | 60 | 720 | 720 | 4-φ42 | 800 | 950 | 1015 | 44 | 24-φ33 | 600 | 725 | 780 | 44 | 20-φ30 |
| 800S47 | 2500 | 1455 | 1200 | 1000 | 2200 | 875 | 1200 | 1000 | 2014 | 1200 | 60 | 720 | 720 | 4-φ42 | 800 | 950 | 1015 | 60 | 24-φ33 | 600 | 725 | 780 | 60 | 20-φ30 |
| 800S76 | 2451 | 1387 | 1300 | 1000 | 2265 | 1000 | 1700 | 1350 | 2105 | 1250 | 70 | 850 | 850 | 4-φ58 | 800 | 950 | 1015 | 60 | 32-φ33 | 600 | 725 | 780 | 60 | 20-φ30 |
| 1200S22 | 3285 | 1695 | 1600 | 1250 | 2800 | 1250 | 2060 | 1060 | 2650 | 1700 | 120 | 870 | 1020 | 8-φ55 | 1200 | 1450 | 1530 | 67 | 32-φ33 | 800 | 990 | 1070 | 67 | 24-φ33 |
| 1200S32 | 3285 | 1695 | 1600 | 1250 | 2800 | 1250 | 2060 | 1060 | 2650 | 1700 | 120 | 870 | 1020 | 8-φ55 | 1200 | 1450 | 1530 | 67 | 32-φ33 | 800 | 990 | 1070 | 67 | 24-φ33 |
| 1200S39 | 3295 | 1695 | 1680 | 1250 | 2800 | 1250 | 2060 | 1060 | 2700 | 1700 | 120 | 870 | 1020 | 8-φ55 | 1200 | 1450 | 1530 | 67 | 32-φ33 | 800 | 990 | 1070 | 67 | 24-φ33 |
| 1200S56 | 3295 | 1695 | 1680 | 1250 | 2800 | 1250 | 2060 | 1060 | 2700 | 1700 | 120 | 870 | 1020 | 8-φ55 | 1200 | 1450 | 1530 | 67 | 32-φ33 | 800 | 990 | 1070 | 67 | 24-φ33 |
| 1200S72 | 3295 | 1695 | 1680 | 1250 | 2800 | 1250 | 2060 | 1060 | 2700 | 1700 | 120 | 870 | 1020 | 8-φ55 | 1200 | 1450 | 1530 | 67 | 32-φ33 | 800 | 990 | 1070 | 67 | 24-φ33 |

S型泵安装尺寸图（带公用底座）

The Overall Dimensions (Have Common Base)

S型泵安装尺寸表（带公用底座）（1）

The Chart Of Overall Dimensiongs(Have Common Base)                       单位：mm

| 泵型号 Type | 电动机 Motor |  |  | 电机尺寸 Motor Size |  |  | 底座尺寸 Common Base |  |  |  |  |  |  | E | H1 | L | 吐出锥管法兰尺寸 Discharge Cone Pipe |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 型号 Type | 功率 Power | 电压 V | L4 | h | H | L1 | L2 | L3 | L5 | b | b1 | n-φd1 |  |  |  | Dg2 | D02 | D2 | n-φd2 |
| 150S50 | Y200L2-2 | 37 | 380 | 794 | 475 | 200 | 1165 | 180 | 750 |  | 390 | 500 | 4-φ25 | 300 | 380 | 1435 | 150 | 240 | 285 | 8-φ23 |
| 150S50A | Y200L1-2 | 30 |  | 677 | 475 | 200 | 1165 | 180 | 750 |  | 390 | 500 |  | 300 | 380 | 1318 |  |  |  |  |
| 150S50B | Y180M-2 | 22 |  | 687 | 430 | 180 | 1077 | 207 | 670 |  | 480 | 480 |  | 300 | 380 | 1318 |  |  |  |  |
| 150S97 | Y280S | 75 |  | 1019 | 640 | 280 | 1415 | 265 | 850 |  | 410 | 640 | 4-φ25 | 300 | 400 | 1718 | 150 | 240 | 285 | 8-φ23 |
| 150S97A | Y280S-2 | 75 |  | 1019 | 640 | 280 | 1415 | 265 | 850 |  | 410 | 640 |  | 300 | 400 | 1718 |  |  |  |  |
| 150S97B | Y160M-4 | 11 |  | 617 | 385 | 160 | 1105 | 205 | 710 |  | 450 | 450 |  | 300 | 400 | 1306 |  |  |  |  |
| 200S95 | Y315M-2 | 132 |  | 1238 | 865 | 315 | 1590 | 250 | 1000 |  | 455 | 730 | 4-φ25 | 375 | 440 | 2102 | 200 | 295 | 340 | 8-φ23 |
| 200S95A | Y315S-2 | 110 |  | 1196 | 865 | 315 | 1590 | 250 | 1000 |  | 455 | 730 |  | 375 | 440 | 1988 |  |  |  |  |
| 200S95B | Y280S-2 | 75 |  | 1006 | 640 | 280 | 1456 | 306 | 850 |  | 455 | 655 |  | 375 | 440 | 1798 |  |  |  |  |
| 150S78 | Y250M-2 | 55 |  | 932 | 575 | 250 | 1360 | 280 | 800 |  | 430 | 585 | 4-φ30 | 300 | 395 | 1663 | 150 | 240 | 285 | 8-φ22 |
| 150S78A | Y225M-2 | 45 |  | 817 | 530 | 225 | 1240 | 280 | 750 |  | 540 | 540 |  | 300 | 395 | 1548.5 |  |  |  |  |
| 150S78B | Y200L2-2 | 37 |  | 777 | 475 | 200 | 1240 | 280 | 680 |  | 504 | 504 |  | 300 | 395 | 1508.5 |  |  |  |  |
| 200S42 | Y250M-2 | 55 |  | 932 | 575 | 250 | 1360 | 230 | 850 |  | 450 | 620 | 4-φ24 | 350 | 465 | 1692 | 200 | 295 | 340 | 8-φ22 |
| 200S42A | Y200L2-2 | 37 |  | 777 | 475 | 200 | 1254 | 230 | 850 |  | 450 | 620 |  | 350 | 465 | 1537 |  |  |  |  |
| 250S14 | Y200L-4 | 30 |  | 777 | 475 | 200 | 1426 | 256 | 940 |  | 600 | 600 | 4-φ28 | 300 | 560 | 1658 | 250 | 350 | 395 | 12-φ22 |
| 250S14A | Y180L-4 | 22 |  | 712 | 430 | 180 | 1426 | 256 | 940 |  | 600 | 600 |  | 300 | 560 | 1593 |  |  |  |  |
| 250S24 | Y250M-4 | 55 |  | 932 | 575 | 250 | 1545 | 209 | 1056 |  | 650 | 650 | 4-φ28 | 300 | 560 | 1901 | 250 | 335 | 375 | 12φ-18 |
| 250S24A | Y200L-4 | 30 |  | 777 | 475 | 200 | 1426 | 256 | 940 |  | 600 | 600 |  | 300 | 560 | 1746 |  |  |  |  |

S型泵安装尺寸表（带公用底座）（2）

The Chart Of Overall Dimensiongs(Have Common Base)                       单位：mm

| 泵型号 Type | 电动机 Motor |  |  | 电机尺寸 Motor Size |  |  | 底座尺寸 Common Base |  |  |  |  |  |  | E | H1 | L | 吐出锥管法兰尺寸 Discharge Cone Pipe |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 型号 Type | 功率 Power | 电压 V | L4 | h | H | L1 | L2 | L3 | L5 | b | b1 | n-φd1 |  |  |  | Dg2 | D02 | D2 | n-φd2 |
| 300S19 | Y250M-4 | 55 | 380 | 932 | 575 | 250 | 1618 | 288 | 1050 |  | 700 | 700 | 4-φ30 | 300 | 620 | 1936 | 300 | 400 | 445 | 12-φ22 |
| 300S19A | Y225M-4 | 45 |  | 847 | 530 | 225 | 1618 | 288 | 1050 |  | 700 | 700 |  | 300 | 620 | 1851 |  |  |  |  |
| 300S12 | Y225S-4 | 37 |  | 822 | 530 | 225 | 1540 | 280 | 980 |  | 700 | 700 | 4-φ30 |  | 620 | 1856 |  |  |  |  |
| 300S12A | Y200L-4 | 30 |  | 777 | 475 | 200 | 1540 | 280 | 980 |  | 700 | 700 |  |  | 620 | 1811 |  |  |  |  |
| 250S39 | Y280S-4 | 75 |  | 1002 | 640 | 280 | 1613 | 250 | 1080 | 540 | 680 | 680 | 6-φ25 | 300 | 550 | 1991 | 250 | 350 | 395 | 12-φ22 |
| 250S39A | Y250M-4 | 55 |  | 932 | 575 | 250 | 1613 | 250 | 1080 | 540 | 680 | 680 |  | 300 | 550 | 1921 |  |  |  |  |
| 250S65 | Y315M-4 | 132 |  | 1342 | 865 | 315 | 1822 | 250 | 1200 | 600 | 610 | 760 | 6-φ25 | 300 | 570 | 2404 | 250 | 350 | 395 | 12-φ22 |
| 250S65A | Y315S-4 | 110 |  | 1272 | 865 | 315 | 1822 | 250 | 1200 | 600 | 610 | 760 |  | 300 | 570 | 2334 |  |  |  |  |
| 350S16 | Y280S-4 | 75 |  | 1002 | 640 | 280 | 1801 | 300 | 1200 | 600 | 825 | 825 | 6-φ40 |  | 720 | 3218 |  |  |  |  |
| 350S16A | Y250M-4 | 55 |  | 932 | 575 | 250 | 1801 | 300 | 1200 | 600 | 825 | 825 |  |  | 720 | 2068 |  |  |  |  |
| 300S32 | Y315S-4 | 110 |  | 1272 | 865 | 315 | 1808 | 300 | 1220 | 610 | 720 | 770 | 6-φ30 | 300 | 610 | 2380 | 300 | 400 | 445 | 12-φ22 |
| 300S32A | Y280S-4 | 75 |  | 1002 | 640 | 280 | 1757 | 2955 | 1160 | 580 | 710 | 710 |  | 300 | 610 | 2110 |  |  |  |  |

S型泵安装尺寸图（不带公用底座）

The Overall Dimensions (Without Common Base)

S型泵安装尺寸表（不带公用底座）（1）

The Chart Of Overall Dimensiongs(Without Common Base)                      单位：mm

| 泵型号 Type | 电动机 Motor |  |  | 泵外形和安装尺寸 Pump Overall and Installation Dimensions |  |  |  |  |  |  |  |  |  | 吐出锥管法兰 Discharge Cone Pipe |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 电机型号 Motor Type | 功率 Power (kw) | 电压 (V) | C | L1 | H | h | B | A | n-φd1 | E | L | L2 | Dg2 | D2 | D02 | b2 | n-φd2 |
| 300S90 | Y355L2-4 | 315 | 380 | 5 | 1572 | 355 | 1035 | 630 | 610 | 4-φ28 | 500 | 2745 | 848 | 300 | 445 | 400 | 28 | 12-φ23 |
| 300S90A | Y355L1-4 | 280 |  |  | 1572 | 355 | 1035 | 630 | 610 | 4-φ28 |  | 2745 | 848 |  |  |  |  |  |
| 300S90B | Y355M1-4 | 220 |  |  | 1572 | 355 | 1035 | 560 | 610 | 4-φ28 |  | 2745 | 848 |  |  |  |  |  |
| 300S58 | Y315M1-4 (IP23) | 185 | 380 | 6 | 1180 | 315 | 865 | 457 | 508 | 4-φ28 | 300 | 2298 | 786 | 300 | 445 | 400 | 28 | 12φ22 |
| 300S58A | Y315L1-4 | 160 |  |  | 1180 | 315 | 865 | 457 | 508 | 4-φ28 |  | 2298 | 786 |  |  |  |  |  |
| 300S58B | Y315M-4 | 132 |  |  | 1180 | 315 | 865 | 508 | 508 | 4-φ28 |  | 2298 | 786 |  |  |  |  |  |
| 300S32 | Y315S-4 | 110 | 380 | 4 | 1270 | 315 | 865 | 406 | 508 | 4-φ28 | 300 | 2376.5 | 781 | 300 | 445 | 400 | 28 | 12-φ22 |
| 300S32A | Y280S-4 | 75 |  |  | 1002 | 280 | 640 | 368 | 457 | 4-φ24 |  | 2108.5 | 725 |  |  |  |  |  |
| 350S125 | Y4502-4 | 710 | 6000 | 7 | 2180 | 450 | 1475 | 1120 | 800 | 4-φ35 | 750 | 3592.5 | 1105 | 350 | 520 | 470 | 36 | 16-φ26 |
| 350S125A | Y4005-4 | 560 |  |  | 2090 | 450 | 1330 | 1000 | 710 | 4-φ35 |  | 3502.5 | 1085 |  |  |  |  |  |
| 350S125B | Y4002-4 | 400 |  |  | 2090 | 400 | 1330 | 1000 | 710 | 4-φ35 |  | 3502.5 | 1085 |  |  |  |  |  |
| 350S75 | Y4002-4 | 400 | 6000 | 5 | 2090 | 400 | 1330 | 1000 | 710 | 4-φ35 | 500 | 3370.5 | 1014 | 350 | 505 | 460 | 30 | 16-φ22 |
| 350S75A | Y3555-4 | 280 |  |  | 1780 | 355 | 1110 | 900 | 630 | 4-φ28 |  | 3060.5 | 994 |  |  |  |  |  |
| 350S75B | Y3553-4 | 220 |  |  | 1780 | 355 | 1110 | 900 | 630 | 4-φ28 |  | 3050.5 | 989 |  |  |  |  |  |
| 350S44 | Y3553-4 | 220 | 6000 | 5 | 1780 | 355 | 1110 | 900 | 630 | 4-φ28 | 300 | 3050.5 | 989 | 350 | 505 | 460 | 30 | 16-φ22 |
| 350S44A | Y315L1-4 | 160 | 380 |  | 1342 | 315 | 760 | 508 | 508 | 4-φ28 |  | 2605.5 | 850 |  |  |  |  |  |
| 350S26 | Y315M-4 | 132 | 380 | 4 | 1342 | 315 | 760 | 457 | 508 | 4-φ28 | 300 | 2519.5 | 787 | 350 | 505 | 460 | 30 | 16-φ22 |
| 350S26A | Y280M-4 | 90 |  |  | 1052 | 280 | 640 | 419 | 457 | 4-φ24 |  | 2229.5 | 731 |  |  |  |  |  |
| 500S13 | Y315S-6 (IP23) | 110 | 380 | 5 | 1160 | 315 | 865 | 406 | 508 | 4-φ28 | 600 | 2480 | 818 | 500 | 620 | 670 | 34 | 20-φ26 |

S型泵安装尺寸表（不带公用底座）（2）

The Chart Of Overall Dimensiongs(Without Common Base)                      单位：mm

| 泵型号 Type | 电动机 Motor |  |  | 泵外形和安装尺寸 Pump Overall and Installation Dimensions |  |  |  |  |  |  |  |  |  | 吐出锥管法兰 Discharge Cone Pipe |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 电机型号 Motor Type | 功率 Power (kw) | 电压 (V) | C | L1 | H | h | B | A | n-φd1 | E | L | L2 | Dg2 | D2 | D02 | b2 | n-φd2 |
| 500S22 | Y355M2-6 | 185 | 380 | 5 | 1570 | 355 | 1035 | 560 | 610 | 4-φ28 | 600 | 2950.5 | 889 | 500 | 620 | 670 | 34 | 20-φ26 |
| 500S22A | Y315M1-6 IP23 | 132 |  |  | 1210 | 315 | 865 | 457 | 508 | 4-φ28 |  | 2592.5 | 853 |  |  |  |  |  |
| 500S35 | Y4002-6 | 280 | 6000 | 6 | 2090 | 400 | 1330 | 1000 | 710 | 4-φ36 | 800 | 3471.5 | 1029 | 500 | 620 | 670 | 34 | 20-φ26 |
| 500S35A | Y3555-6 | 220 |  |  | 1780 | 355 | 1110 | 900 | 630 | 4-φ28 |  | 3161.5 | 1009 |  |  |  |  |  |
| 500S59 | Y4501-6 | 450 | 6000 | 7 | 2180 | 450 | 1475 | 1120 | 800 | 4-φ36 | 800 | 3826.5 | 1189 | 500 | 620 | 670 | 34 | 20-φ26 |
| 500S59A | Y4005-6 | 400 |  |  | 2090 | 400 | 1330 | 1000 | 710 | 4-φ36 |  | 3736.5 | 1169 |  |  |  |  |  |
| 500S59B | Y4003-6 | 315 |  |  | 2090 | 400 | 1330 | 1000 | 710 | 4-φ36 |  | 3736.5 | 1169 |  |  |  |  |  |
| 500S98 | Y5002-6 | 800 | 6000 | 7 | 2550 | 500 | 1655 | 1250 | 900 | 4-φ42 | 1000 | 4198.5 | 1356 | 500 | 620 | 670 | 34 | 20-φ26 |
| 500S98A | Y4504-6 | 630 |  |  | 2180 | 450 | 1475 | 1120 | 800 | 4-φ36 |  | 3828.5 | 1196 |  |  |  |  |  |
| 500S98B | Y4503-6 | 560 |  |  | 2180 | 450 | 1475 | 1120 | 800 | 4-φ36 |  | 3828.5 | 1196 |  |  |  |  |  |
| 600S32 | Y4005-6 | 400 |  | 6 | 1862 | 400 | 1200 | 1000 | 710 | 4-φ35 |  | 4048 | 1306 |  |  |  |  |  |
| 600S32A | Y3556-6 | 250 |  |  | 1722 | 355 | 1070 | 900 | 630 | 4-φ28 |  | 3908 | 1286 |  |  |  |  |  |
| 600S47 | Y4503-6 | 560 | 6000 | 7 | 2077 | 450 | 1350 | 1120 | 800 | 4-φ35 | 250 | 3778 | 1174 | 400 | 515 | 565 |  | 16-φ26 |
| 600S75 | Y5003-6 | 900 | 6000 | 7 | 2220 | 500 | 1795 | 1250 | 900 | 4-φ42 |  | 4335 | 1431 |  |  |  |  |  |
| 600S75A | Y4504-6 | 630 |  |  | 2077 | 450 | 1350 | 1120 | 800 | 4-φ35 |  | 4992 | 1311 |  |  |  |  |  |
| 800S22 | Y4504-8 | 450 | 6000 | 6 | 2220 | 500 | 1795 | 1250 | 900 | 4-φ42 | 800 | 4190 | 1191 | 800 | 950 | 1015 | 44 | 24-φ33 |
| 800S22J | Y4502-10 | 250 |  |  | 2080 | 450 | 1350 | 1120 | 800 | 4-φ35 |  | 4190 | 1191 |  |  |  |  |  |
| 800S22A | Y4501-8 | 315 |  |  | 2080 | 450 | 1350 | 1120 | 800 | 4-φ35 |  | 4190 | 1191 |  |  |  |  |  |
| 800S22JA | Y355L-10 | 185 | 380 |  | 2080 | 450 | 1350 | 1120 | 800 | 4-φ35 |  | 3700 | 1050 |  |  |  |  |  |

S型泵安装尺寸表（不带公用底座）（3）

The Chart Of Overall Dimensiongs(Without Common Base)                      单位：mm

| 泵型号 Type | 电动机 Motor |  |  | 泵外形和安装尺寸 Pump Overall and Installation Dimensions |  |  |  |  |  |  |  |  |  | 吐出锥管法兰 Discharge Cone Pipe |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 电机型号 Motor Typr | 功率Power (kw) | 电压 (V) | C | L1 | H | h | B | A | n-φd1 | E | L | L2 | Dg2 | D2 | D02 | b2 | n-φd2 |
| 800S32 | Y4504-6 | 630 | 6000 | 6 | 2077 | 450 | 1350 | 1120 | 800 | 4-φ35 | 800 | 4530 | 1457 | 800 | 950 | 1015 | 44 | 24-φ33 |
| 800S32A | Y4504-8 | 450 |  |  | 2080 | 450 | 1350 | 1120 | 800 | 4-φ35 |  | 4396 | 1330 |  |  |  |  |  |
| 800S47 | Y5603-8 | 1000 | 6000 | 8 | 2900 | 560 | 1700 | 1400 | 1000 | 4-φ42 | 800 | 5408 | 1765 | 800 | 950 | 1015 | 44 | 24-φ33 |
| 800S47J | Y5002-10 | 450 |  |  | 2220 | 500 | 1795 | 1250 | 900 | 4-φ42 |  | 4730 | 1593 |  |  |  |  |  |
| 800S47A | Y5004-8 | 710 |  |  | 2220 | 500 | 1795 | 1250 | 900 | 4-φ42 |  | 4730 | 1593 |  |  |  |  |  |
| 800S47JA | Y4505-10 | 355 |  |  | 2080 | 450 | 1650 | 1120 | 800 | 4-φ35 |  | 4590 | 1473 |  |  |  |  |  |
| 800S76 | Y6304-8 | 1600 | 6000 | 8 | 3102 | 630 | 1900 | 1600 | 1120 | 4-φ48 | 800 | 5561 | 1677 | 800 | 950 | 1015 | 44 | 24-φ33 |
| 800S76A | Y6303-8 | 1400 |  |  | 3102 | 630 | 1900 | 1600 | 1120 | 4-φ48 |  | 5561 | 1677 |  |  |  |  |  |
| 800S76B | Y6303-8 | 1250 |  |  | 3102 | 630 | 1900 | 1600 | 1120 | 4-φ48 |  | 5561 | 1677 |  |  |  |  |  |
| 800S76J | Y6301-10 | 1000 |  |  | 3102 | 630 | 1900 | 1600 | 1120 | 4-φ48 |  | 5561 | 1677 |  |  |  |  |  |
| 1200S22 | Y6302-12 | 800 | 6000 | 7 | 3102 | 630 | 1900 | 1600 | 1120 | 4-φ48 | 800 | 6394 | 1860 | 800 | 990 | 1070 |  | 24-φ34 |
| 1200S22A | Y6301-12 | 710 |  |  | 3102 | 630 | 1900 | 1600 | 1120 | 4-φ48 |  | 6394 | 1860 |  |  |  |  |  |
| 1200S32 | Y6304-10 | 1400 | 6000 | 8 | 3102 | 630 | 1900 | 1600 | 1120 | 4-φ48 | 800 | 6394 | 1860 | 800 | 990 | 1070 |  | 24-φ34 |
| 1200S32A | Y6303-10 | 1250 |  |  | 3102 | 630 | 1900 | 1600 | 1120 | 4-φ48 |  | 6394 | 1860 |  |  |  |  |  |
| 1200S39 | Y800-1-12 | 1600 | 6000 | 8 | 3422 | 800 | 2550 | 2000 | 1600 | 4-φ56 | 800 | 6725 | 1960 | 800 | 990 | 1070 |  | 24-φ34 |
| 1200S39A | Y710-2-12 | 1250 |  |  | 3202 | 710 | 2330 | 1800 | 1400 | 4-φ56 |  | 6505 | 1960 |  |  |  |  |  |
| 1200S39B | Y6304-12 | 1000 |  |  | 3102 | 630 | 1900 | 1600 | 1120 | 4-φ48 |  | 6405 | 1860 |  |  |  |  |  |
| 1200S56 | Y800-1-10 | 2240 | 6000 | 9 | 3422 | 800 | 2550 | 2000 | 1600 | 4-φ56 | 800 | 6726 | 1961 | 800 | 990 | 1070 |  | 24-φ34 |
| 1200S56A | Y710-3-10 | 2000 |  |  | 3202 | 710 | 2330 | 1800 | 1400 | 4-φ56 |  | 6506 | 1961 |  |  |  |  |  |
| 1200S56B | Y710-1-10 | 1600 |  |  | 3202 | 710 | 2330 | 1800 | 1400 | 4-φ56 |  | 6506 | 1961 |  |  |  |  |  |
| 1200S72 | Y800-2-10 | 2500 | 6000 | 9 | 3422 | 800 | 2550 | 2000 | 1600 | 4-φ56 | 800 | 6726 | 1961 | 800 | 990 | 1070 |  | 24-φ34 |