IS、IR、IY型单吸单级离心泵

安装使用说明书

长沙福斯水泵泵业有限公司

Fuchs Changsha Pump pump industry limited company

概  述

General

IS型泵是单级单吸（轴向吸入）离心泵，供输送温度低于80℃的清水或物理、化学性质类似于水的其他液体，泵的进口压力小于0.3MPa，适用于工业和城市给排水及农业排灌。

IR型热水离心泵是在IS型单级离心泵的基础上派生的节能产品，该系列产品设计合理，安装维修方便，适用于输送温度低于130℃的清水或物理、化学性质类似于水的介质。泵的吸入口压力不大于0.6Mpa，可用于热水锅炉及与换热器配套，作为循环水泵，给水泵，也可作其他用途的输水泵，如城市给排水和矿山排水等。

IY型单级单吸输油离心泵，适用于输送不含固体颗粒，粘度小于120厘沲的无腐蚀类和石油产品。也供输送清水或物理及化学性质类似于清水的其他液体，温度不高于80℃，进口压力不大于0.3MPa。

Type IS pump is single stage single suction(axial suction) centrifugal pump, deliver clean water or other liquid which chemical & physical feature is similar with clean water, the temperature is less than 80℃.Inlet pressure is less than 0.3MPa, it is suitable for delivering water in industry, city and farm irrigation.

Type IR pump is heat centrifugal pump, the serial pump design reasonable, installing & repairing conveniently, it suitable for delivery clean water or which chemical & physical feature is similar with clean water. Inlet pressure is less than 0.3MPa, the temperature is not more than 130℃.it can equipped with boiler and heat-changer, as circulating water pump or feed pump, also used to supply water, for example, supply water in city and mine etc.

Type IY pump is single stage single suction centrifugal oil pump, suitable for delivery no corrosive liquids and petroleum products, which is not contain solids and the Viscosity is less than 120Cst. Also used to deliver clean water or other liquid which chemical & physical feature is similar with clean water, the temperature is less than 80℃.Inlet pressure is less than 0.3MPa

性 能 范 围（设 计 点）

Performance Range(design point)

流量 Capacity：6.3~400m3/h

扬程 Head：5~125m

型 号 意 义

Type Description

IS（IR、IY）80-65-125A

IS—单级单吸清水离心泵           IS—Single-stage single-suction clean water centrifugal pump

IR—单级单吸热水离心泵           IR—Single-stage single-suction heat wate centrifugal pump

IY—单级单吸输油离心泵           IY—Single-stage single-suction centrifugal oil pump

80—泵入口直径为80mm            80—Inlet diameter is 80mm

65—泵出口直径为65mm            65—Outlet diameter is 65mm

125—叶轮名义直径125mm          125— Impeller nominal diameter is125mm

A—叶轮外径 切割代号（A、B、C    A—The code of impeller is cut (A、B、C stand

分别表示第一、二、三次切割）        for first cut, second cut and third cut respectively )

结 构 特 点

Construction feature

IS型泵是根据国际标准IS02858所规定的的性能和尺寸设计的。泵主要由泵体、泵盖、叶轮、轴、密封部件和悬架部件等组成。

泵的结构采取后开门的结构形式，即泵体与泵盖的分界在叶轮背面，泵体和泵盖构成泵的工作室；叶轮、轴和滚动轴承等为泵的转子；悬架和轴承部件支撑泵的转子。为了平衡泵的轴向力，大多数叶轮前、后均设有密封环，并在叶轮后盖板上设有平衡孔。但有些泵的轴向力不大，叶轮背面不必设密封环和平衡孔。

IR、IY型泵结构形式与IS型泵基本相同，IR型泵泵盖与水冷室盖组成水冷室，用于可靠地冷却填料、轴及阻止热量向轴承传递。

轴承 采用两个向心球轴承（IR泵为一个向心球轴承，两个向心推力球轴承）装在悬架内，支撑泵轴，承受泵的径向力与轴向力。

轴封 IS型泵采用填料密封，在轴封处装有轴套以保护轴；也可根据用户要求装配机械密封。

IR型泵的轴向密封采用填料密封和机械密封两种方式，泵盖上设有内水封孔，外水封孔和冷却腔。

IY 型泵的轴向密封采用机械密封，也可根据用户要求装配填料密封。

密封和冷却方式有以下几种：

- 填料密封 体内水封 不接冷却水；

- 填料密封 体内水封 接冷却水；

- 填料密封 体外水封 不接冷却水；

- 填料密封 体外水封 接冷却水；

- 机械密封 不接冷却水；

- 机械密封 接冷却水。

Type IS pump is designed according to National Standard ISO2858.Main parts are pump casing, pump cover, impeller, shaft, sealing parts and cantilever parts etc.

IS pump is designed at full back pullout, the pump casing and pump cover is separate from impeller back face, Pump casing and pump cover are combined a working house; impeller, shaft, and rolling bearing are combined a rotor; cantilever support and bearing parts support the rotor. To balance the axial force, impeller rear cover have balance holes, impeller have wearing. If the axial force is small, the impeller rear back hasn’t wearing and balance holes.

IR pump have same construction type with IS pump, pump cover and sealing hose are combined a cooling house, used for cooling packing and shaft, and prevent heat sending to bearing.

Bearing: adopt two radial ball bearing, (IR pump is one set radial ball bearing, two set radial thrust-force ball bearing), installed in cantilever support, to support pump shaft, and bear pump axial force and radial force.

Seal: IS pump is adopted packing seal, in seal, shaft sleeve is installed to protect shaft; mechanical seal can be used according to user requirement.

IR pump seal have two type: packing seal and mechanical seal, in pump cover have water sealing hole, outer water sealing hole and cooling house.

IY pump is adopted mechanical seal; packing seal can be used according to user requirement.

Type of sealing and cooling has several kinds as follow:

- packing sealing: itself water sealing without cooling water

- packing sealing: itself water sealing with cooling water

- packing sealing: outer water sealing without cooling water

- packing sealing: outer water sealing with cooling water

- mechanical seal: without cooling water

- mechanical seal: with cooling water

各种密封和冷却方式的适用条件见下表：

All kinds seal and cooling condition as follow:

| 介质温度（℃） Medium temperature | ≤80 | ＞80~100 | ≥100~150 |
| --- | --- | --- | --- |
| 密封与冷却方式 Type of seal and cooling | (1) (5) | (2)(3)(5) | (4)(6) |

冷却水压力：P=0.15~0.3Mpa，水封水压力比轴封前大0.05~0.1MPa

水封水需水量：0.2~0.5m3/h

冷却水需水量：0.3~0.7 m3/h

传动 通过弹性联轴器由电动机直接驱动；从电机端看，泵为顺时针方向旋转。

Cooling water pressure: P=0.05-0.3MPa, the Sealing water pressure is over 0.05-0.1MPa than sealing house.

Sealing water flow: 0.2-0.5m3/h

Cooling water flow: 0.3-0.7m3/h

Driver: pump is driver by motor directly through flexible coupling; view from motor end, the rotating direction is clockwise.

材料

Material

| 零件名称Part name | 材料Material | 零件名称 part name | 材料Material |
| --- | --- | --- | --- |
| 泵体pump casing | HT200 | 泵轴shaft | 45 |
| 泵盖pump cover | HT200 | 叶轮impeller | HT200 |
| 密封环wearing | HT200 | 轴套shaft sleeve | HT200 |

注：材料可根据用户要求选配。

Note: the material can be supplied according to user requirement.

IS、IY型泵结构图

IS、IY pump construction Drawing

1、泵体         1、pump casing

2、叶轮螺母     2、impeller nut

3、止动垫圈     3、gasket

4、密封环*      4、wearing*

5、叶轮         5、impeller

6、泵盖       6、pump cover

7、轴套*      7、shaft sleeve*

8、填料环*    8、packing ring*

9、填料       9、packing

10、填料压盖  10、packing cover

11、悬架轴承部 11、cantilever

bearing part

12、轴         12、shaft

带*号表示易损件

It is wearable part with symbol *

IR型泵结构图

IR pump construction Drawing

1、泵体         pump casing

2、叶轮螺母    impeller nut

3、止动垫圈    gasket

4、密封环*     wearing*

5、叶轮        impeller

6、泵盖        pump cover

7、轴套*       shaft sleeve*

8、填料环*     packing ring*

9、水冷室盖    cooling house cover

10、填料        Packin

11、水冷填料压盖或填料压盖

packing cover or cooling water

packing cover

12、悬架轴承部

Cantilever bearing part

13、轴  shaft

14、机械密封  mechanical seal

15、机械密封压盖

mechanical seal cove

带*号表示易损件

It is wearable part with symbol *

型谱图

Available head-capacity cues

| 性能参数表 # Sheet of Performance Date |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 参数 Date 型号 Type | 流量 |  | 扬程 | 转速 | 轴功率 | 电机motor |  | 效率 Eff η | 必需汽蚀余量NPSHr | 泵口径 |  | 泵重 Pump weight |
|  | Flow |  | Head | Spead | Shart power | 功率Power | 型号 Type |  |  | 吸入 Suction dia | 吐出 Discharge dia |  |
|  | m3/h | L/s | m | r/min | kW | kW |  | % | m | mm | mm | kg |
| IS IR50-32-125 IY | 7.5 12.5 15 | 2.08 3.14 4.17 | 22 20 18.5 | 2900 | 0.96 1.13 1.26 | 2.2 | Y90L-2 | 47 60 60 | 2.0 2.0 2.5 | 50 | 32 | 40 |
|  | 3.75 6.3 7.5 | 1.04 1.74 2.08 | 5.4 5 4.6 | 1450 | 0.13 0.16 0.17 | 0.55 | Y801-4 | 43 54 55 | 2.0 2.0 2.5 |  |  |  |
| IS IR50-32-125A IY | 6.75 11.25 13.5 | 1.87 3.12 3.75 | 17.8 16.2 15 | 2900 | 0.71 0.84 0.94 | 1.5 | Y90S-2 | 46 59 59 | 2.0 2.0 2.5 | 50 | 32 | 40 |
| IS IR50-32-125B IY | 6 10 12 | 1.67 2.78 3.33 | 14.1 12.8 11.8 | 2900 | 0.51 0.6 0.67 | 1.1 | Y802-2 | 45 58 58 | 2.0 2.0 2.5 | 50 | 32 | 40 |
| IS IR50-32-160 IY | 7.5 12.5 15.0 | 2.08 3.47 4.17 | 34.3 32.0 29.6 | 2900 | 1.59 2.02 2.16 | 3.0 | Y100L-2 | 44 54 56 | 2.0 2.0 2.5 | 50 | 32 | 40 |
|  | 3.75 6.3 7.5 | 1.04 1.74 2.08 | 8.5 8.0 7.5 | 1450 | 0.25 0.29 0.31 | 0.55 | Y801-4 | 35 48 49 | 2.0 2.0 2.5 |  |  |  |
| IS IR50-32-160A IY | 6.75 11.25 13.5 | 1.87 3.12 3.75 | 27.8 26.0 24.0 | 2900 | 1.19 1.50 1.60 | 2.2 | Y90L-2 | 43 53 55 | 2.0 2.0 2.5 | 50 | 32 | 40 |
| IS IR50-32-160B IY | 6 10 12 | 1.67 2.78 3.33 | 22.0 20.5 18.9 | 2900 | 0.86 1.07 1.14 | 1.5 | Y90S-2 | 42 52 54 | 2.0 2.0 2.5 | 50 | 32 | 40 |
| IS IR50-32-200 IY | 7.5 12.5 15.0 | 2.08 3.47 4.17 | 52.5 50.0 48.0 | 2900 | 2.82 3.55 3.85 | 5.5 | Y132S1-2 | 38 48 51 | 2.0 2.0 2.5 | 50 | 32 | 43 |
|  | 3.75 6.3 7.5 | 1.04 1.74 2.08 | 13.1 12.5 12.0 | 1450 | 0.41 0.51 0.56 | 0.75 | Y802-4 | 33 42 44 | 2.0 2.0 2.5 |  |  |  |
| IS IR50-32-200A IY | 6.75 11.25 13.5 | 1.87 3.12 3.75 | 42.5 40.5 38.9 | 2900 | 2.11 2.65 2.94 | 4.0 | Y112M-2 | 37 47 50 | 2.0 2.0 2.5 | 50 | 32 | 43 |
| IS IR50-32-200B IY | 6.0 10.0 12.0 | 1.67 2.78 3.33 | 33.6 32.0 30.7 | 2900 | 1.53 1.90 2.05 | 3 | Y100L-2 | 36 46 49 | 2.0 2.0 2.5 | 50 | 32 | 43 |
| IS IR50-32-250 IY | 7.5 12.5 15.0 | 2.08 3.47 4.17 | 82.0 80.0 78.5 | 2900 | 5.87 7.16 7.83 | 11 | Y160M1-2 | 28.5 38 41 | 2.0 2.0 2.5 | 50 | 32 | 76 |
| IS IR50-32-250 IY | 3.75 6.3 7.5 | 1.04 1.74 2.08 | 20.5 20 19.5 | 1450 | 0.91 1.07 1.14 | 1.5 | Y90L-4 | 23 32 35 | 2.0 2.0 2.5 | 50 | 32 | 76 |
| IS IR50-32-250A IY | 6.75 11.25 13.5 | 1.87 3.12 3.75 | 66.4 64.8 63.6 | 2900 | 4.44 5.35 5.85 | 7.5 | Y132S2-2 | 27.5 37 40 | 2.0 2.0 2.5 | 50 | 32 | 76 |
|  | 3.35 5.62 6.75 | 0.94 1.56 1.87 | 16.6 16.2 15.9 | 1450 | 0.69 0.80 0.86 | 1.1 | Y90S-4 | 22 31 34 | 2.0 2.0 2.5 |  |  |  |
| IS IR65-50-125 IY | 15.0 25.0 30.0 | 4.17 6.94 8.33 | 21.8 20.0 18.5 | 2900 | 1.54 1.97 2.22 | 3.0 | Y100L-2 | 58 69 68 | 2.0 2.0 3.0 | 65 | 50 | 40 |
|  | 7.5 12.5 15.0 | 2.08 3.47 4.17 | 5.4 5.0 4.6 | 1450 | 0.21 0.27 0.30 | 0.55 | Y801-4 | 53 64 65 | 2.0 2.0 2.5 |  |  |  |
| IS IR65-50-125A IY | 14.25 23.75 28.5 | 3.96 6.59 7.91 | 19.7 18.1 16.7 | 2900 | 1.34 1.72 1.94 | 2.2 | Y90L-2 | 57 68 67 | 2.0 2.0 3.0 | 65 | 50 | 40 |
| IS IR65-50-125B IY | 12.75 21.25 25.5 | 3.54 5.90 7.08 | 15.8 14.5 13.4 | 2900 | 0.98 1.25 1.40 | 1.5 | Y90S-2 | 56 67 66 | 2.0 2.0 3.0 | 65 | 50 | 40 |
| IS IR65-50-160 IY | 15.0 25.0 30.0 | 4.17 6.94 8.33 | 35.0 32.0 30.0 | 2900 | 2.65 3.35 3.71 | 5.5 | Y132S1-2 | 54 65 66 | 2.0 2.0 2.5 | 65 | 50 | 46 |
|  | 7.5 12.5 15.0 | 2.08 3.47 4.17 | 8.8 8.0 7.5 | 1450 | 0.36 0.45 0.51 | 0.75 | Y802－4 | 50 60 60 | 2.0 2.0 2.5 |  |  |  |
| IS IR65-50-160A IY | 14.25 23.75 28.5 | 3.96 6.59 7.91 | 31.6 28.9 27.1 | 2900 | 2.31 2.92 3.23 | 4 | Y112M－2 | 53 64 65 | 2.0 2.0 2.5 | 65 | 50 | 46 |
| IS IR65-50-160B IY | 12.75 21.25 25.5 | 3.54 5.90 7.08 | 25.3 23.1 21.7 | 2900 | 1.69 2.13 2.35 | 3 | Y100L-2 | 52 63 64 | 2.0 2.0 2.5 | 65 | 50 | 46 |
| IS IR65-40-200 IY | 15.0 25.0 30.0 | 4.17 6.94 8.33 | 53.0 50.0 47.0 | 2900 | 4.42 5.67 6.30 | 7.5 | Y132S2-2 | 49 60 61 | 2.0 2.0 2.5 | 65 | 40 | 50 |
|  | 7.5 12.5 15.0 | 2.08 3.47 4.17 | 13.2 12.5 11.8 | 1450 | 0.63 0.77 0.85 | 1.1 | Y90S-4 | 43 55 57 | 2.0 2.0 2.5 |  |  |  |
| IS IR65-40-200A IY | 12.0 20.0 24.0 | 3.33 5.56 6.67 | 33.9 32.0 30.1 | 2900 | 2.31 2.96 3.28 | 4 | Y112M－2 | 48 59 60 | 2.0 2.0 2.5 | 65 | 40 | 50 |
|  | 6.0 10.0 12.0 | 1.67 2.78 3.33 | 8.5 8.0 7.6 | 1450 | 0.33 0.40 0.45 | 0.75 | Y802－4 | 42 54 56 | 2.0 2.0 2.5 |  |  |  |
| IS IR65-40-250 IY | 15.0 25.0 30.0 | 4.17 6.94 8.33 | 82.0 80.0 78.0 | 2900 | 9.05 10.89 12.02 | 15 | Y160M2－2 | 37 50 53 | 2.0 2.0 2.5 | 65 | 40 | 80 |
|  | 7.5 12.5 15.0 | 2.08 3.47 4.17 | 21.0 20.0 19.4 | 1450 | 1.23 1.48 1.65 | 2.2 | Y100L1－4 | 35 46 48 | 2.0 2.0 2.5 |  |  |  |
| IS IR65-40-250A IY | 12.0 20.0 24.0 | 3.33 5.56 6.67 | 52.5 51.2 49.9 | 2900 | 4.76 5.70 6.28 | 7.5 | Y132S2-2 | 36 49 52 | 2.0 2.0 2.5 | 65 | 40 | 80 |
|  | 6.0 10.0 12.0 | 1.67 2.78 3.33 | 13.1 12.8 12.5 | 1450 | 0.63 0.78 0.87 | 1.5 | Y90L-4 | 34 45 47 | 2.0 2.0 2.5 |  |  |  |
| IS IR65-40-315 IY | 15.0 25.0 30.0 | 4.17 6.94 8.33 | 127.0 125.0 123.0 | 2900 | 18.5 21.3 22.8 | 30 | Y200L1－2 | 28 40 44 | 2.5 2.5 3.0 | 65 | 40 | 106 |
|  | 7.5 12.5 15.0 | 2.08 3.47 4.17 | 32.3 32.0 31.7 | 1450 | 2.63 2.94 3.16 | 4 | Y112M－2 | 25 37 41 | 2.5 2.5 3.0 | 65 | 40 | 106 |
| IS IR65-40-315A IY | 13.5 22.5 27.0 | 3.75 6.25 7.5 | 102.9 101.3 99.6 | 2900 | 14.0 15.9 17.04 | 22 | Y180M-2 | 27 39 43 | 2.5 2.5 3.0 | 65 | 40 | 106 |
|  | 6.73 11.23 13.5 | 1.87 3.12 3.75 | 25.7 25.3 24.9 | 1450 | 1.96 2.15 2.29 | 3 | Y100L2－4 | 24 36 40 | 2.5 2.5 3.0 |  |  |  |
| IS IR65-40-315B IY | 12.85 21.24 25.49 | 3.57 5.90 7.08 | 81.3 80.0 78.7 | 2900 | 10.95 12.18 13.01 | 18.5 | Y160L-2 | 26 38 42 | 2.5 2.5 3.0 | 65 | 40 | 106 |
| IS IR80-65-125 IY | 30.0 50.0 60.0 | 8.33 13.89 16.67 | 22.5 20.0 18.0 | 2900 | 2.87 3.63 3.98 | 5.5 | Y132S1-2 | 64 75 74 | 3.0 3.0 3.5 | 80 | 65 | 43 |
|  | 15.0 25.0 30.0 | 4.17 6.94 8.33 | 5.6 5.0 4.5 | 1450 | 0.42 0.48 0.51 | 0.75 | Y802－4 | 55 71 72 | 2.5 2.5 3.0 |  |  |  |
| IS IR80-65-125A IY | 28.5 47.5 57.0 | 7.92 13.19 15.83 | 20.3 18.1 16.3 | 2900 | 2.50 3.16 3.46 | 4 | Y112M-2 | 63 74 73 | 3.0 3.0 3.5 | 80 | 65 | 43 |
| IS IR80-65-125B IY | 25.5 42.5 51.0 | 7.08 11.82 14.17 | 16.3 14.5 13.0 | 2900 | 1.83 2.29 2.51 | 3 | Y100L-2 | 62 73 72 | 3.0 3.0 3.5 | 80 | 65 | 43 |
| IS IR80-65-160 IY | 30.0 50.0 60.0 | 8.33 13.89 16.67 | 36.0 32.0 29.0 | 2900 | 4.82 5.97 6.59 | 7.5 | Y132S2-2 | 61 73 72 | 2.2 2.5 3.0 | 80 | 65 | 44 |
| IS IR80-65-160 IY | 15.0 25.0 30.0 | 4.17 6.94 8.33 | 9.0 8.0 7.2 | 1450 | 0.67 0.79 0.86 | 1.5 | Y90L－4 | 55 69 68 | 2.0 2.0 2.5 | 80 | 65 | 44 |
| IS IR80-65-160A IY | 24.0 40.0 48.0 | 6.67 11.12 13.33 | 23.0 20.5 18.6 | 2900 | 2.51 3.10 3.42 | 4 | Y112M-2 | 60 72 71 | 2.5 2.5 3.0 | 80 | 65 | 44 |
|  | 12.0 20.0 24.0 | 3.33 5.56 6.67 | 5.8 5.1 4.6 | 1450 | 0.35 0.41 0.45 | 1.1 | Y90S－4 | 54 68 67 | 2.5 2.5 3.0 |  |  |  |
| IS IR80-50-200 IY | 30.0 50.0 60.0 | 8.33 13.89 16.67 | 53.0 50.0 47.0 | 2900 | 7.88 9.87 10.8 | 15 | Y160M2-2 | 55 69 71 | 2.5 2.5 3.0 | 80 | 65 | 48 |
|  | 15.0 25.0 30.0 | 4.17 6.94 8.33 | 13.2 12.5 11.8 | 1450 | 1.06 1.31 1.44 | 2.2 | Y100L1-4 | 51 65 67 | 2.5 2.5 3.0 |  |  |  |
| IS IR80-50-200A IY | 25.5 42.5 51.0 | 7.08 11.8 14.17 | 38.3 36.1 34.0 | 2900 | 4.92 6.15 6.77 | 7.5 | Y132S2-2 | 54 68 70 | 2.5 2.5 3.0 | 80 | 65 | 48 |
|  | 12.75 21.25 25.5 | 3.54 5.90 7.08 | 9.6 9.0 8.5 | 1450 | 0.66 0.81 0.89 | 1.5 | Y90L－4 | 50 64 66 | 2.5 2.5 3.0 |  |  |  |
| IS IR80-50-200B IY | 24.0 40.0 48.0 | 6.67 11.11 13.33 | 33.92 32.0 30.1 | 2900 | 4.19 5.21 5.71 | 7.5 | Y132S2-2 | 53 67 69 | 2.5 2.5 3.0 | 80 | 65 | 48 |
|  | 12.0 20.0 24.0 | 3.33 5.56 6.67 | 8.5 8.0 7.6 | 1450 | 0.56 0.69 0.76 | 1.1 | Y90S－4 | 49 63 65 | 2.5 2.5 3.0 |  |  |  |
| IS IR80-50-250 IY | 30.0 50.0 60.0 | 8.33 13.89 16.67 | 84.0 80.0 74.0 | 2900 | 13.2 17.3 19.2 | 22 | Y180M－2 | 52 63 64 | 2.5 2.5 3.0 | 80 | 65 | 86 |
| IS IR80-50-250 IY | 15.0 25.0 30.0 | 4.17 6.94 8.33 | 21.0 20.0 18.5 | 1450 | 1.75 2.27 2.52 | 3 | Y100L2-4 | 49 60 61 | 2.5 2.5 3.0 | 80 | 65 | 86 |
| IS IR80-50-250A IY | 27.0 45.0 54.0 | 7.5 12.5 15.0 | 68.0 64.0 60.8 | 2900 | 9.81 12.81 14.22 | 18.5 | Y160L-2 | 51 62 63 | 2.5 2.5 3.0 | 80 | 65 | 86 |
| IS IR80-50-250B IY | 25.5 42.5 51.0 | 7.08 11.8 14.17 | 60.7 57.8 54.2 | 2900 | 8.43 10.97 12.17 | 15 | Y160M2-2 | 50 61 62 | 2.5 2.5 3.0 | 80 | 65 | 86 |
| IS IR80-50-315 IY | 30.0 50.0 60.0 | 8.33 13.89 16.67 | 128.0 125.0 123.0 | 2900 | 25.5 31.5 35.5 | 37 | Y200L1-2 | 41 54 57 | 2.5 2.5 3.0 | 80 | 50 | 109 |
| IS IR80-50-315 IY | 15.0 25.0 30.0 | 4.17 6.94 8.33 | 32.5 32.0 31.5 | 1450 | 3.4 4.19 4.6 | 5.5 | Y132S-4 | 39 52 56 | 2.5 2.5 3.0 | 80 | 50 | 109 |
| IS IR80-50-315A IY | 24.0 40.0 48.0 | 6.67 11.11 13.33 | 81.9 80.0 78.7 | 2900 | 13.39 16.43 18.39 | 22 | Y180M-2 | 40 53 56 | 2.5 2.5 3.0 | 80 | 50 | 109 |
|  | 12.0 20.0 24.0 | 3.33 5.56 6.67 | 20.8 20.5 20.2 | 1450 | 1.97 2.19 2.4 | 4 | Y112M-4 | 38 51 55 | 2.5 2.5 3.0 |  |  |  |
| IS IR100-80-125 IY | 60.0 100.0 120.0 | 16.67 27.78 33.33 | 24.0 20.0 16.5 | 2900 | 5.86 7.0 7.28 | 11 | Y160M1-2 | 67 78 74 | 4.0 4.5 5.0 | 100 | 80 | 58 |
|  | 30.0 50.0 60.0 | 8.33 13.89 16.67 | 6.0 5.0 4.0 | 1450 | 0.77 0.91 0.92 | 1.5 | Y90L－4 | 64 75 71 | 2.5 2.5 3.0 |  |  |  |
| IS IR100-80-125A IY | 57.0 95.0 114.0 | 15.83 26.39 31.67 | 21.7 18.1 14.9 | 2900 | 5.10 6.08 6.33 | 7.5 | Y132S2-2 | 66 77 73 | 4.0 4.5 5.0 | 100 | 80 | 58 |
|  | 28.5 47.5 57.0 | 7.92 13.19 15.83 | 5.4 4.5 3.6 | 1450 | 0.67 0.79 0.80 | 1.1 | Y90S－4 | 63 74 70 | 2.5 2.5 3.0 |  |  |  |
| IS IR100-80-125B IY | 51.0 85.0 102.0 | 14.17 23.61 28.33 | 17.34 14.45 11.92 | 2900 | 3.71 4.40 4.60 | 5.5 | Y132S1-2 | 65 76 72 | 4.0 4.5 5.0 | 100 | 80 | 58 |
|  | 25.5 42.5 51.0 | 7.08 11.8 14.17 | 4.3 3.6 2.9 | 1450 | 0.49 0.57 0.58 | 0.75 | Y802－4 | 62 73 69 | 2.5 2.5 3.0 |  |  |  |
| IS IR100-80-160 IY | 60.0 100.0 120.0 | 16.67 27.78 33.33 | 36.0 32.0 28.0 | 2900 | 8.42 11.2 12.2 | 15 | Y160M2-2 | 70 78 75 | 3.5 4.0 5.0 | 100 | 80 | 79 |
|  | 30.0 50.0 60.0 | 8.33 13.89 16.67 | 9.2 8.0 6.8 | 1450 | 1.12 1.46 1.57 | 2.2 | Y100L1-4 | 67 75 71 | 2.0 2.5 3.5 |  |  |  |
| IS IR100-80-160A IY | 54.0 90.0 108.0 | 15.0 25.0 30.0 | 29.16 25.92 22.68 | 2900 | 6.22 8.26 9.02 | 11 | Y160M1-2 | 69 77 74 | 3.5 4.0 5.0 | 100 | 80 | 79 |
|  | 27.0 45.0 54.0 | 7.5 12.5 15.0 | 7.5 6.5 5.5 | 1450 | 0.83 1.07 1.16 | 1.5 | Y90L-4 | 66 74 70 | 2.0 2.5 3.0 |  |  |  |
| IS IR100-65-200 IY | 60.0 100.0 120.0 | 16.67 27.78 33.33 | 54.0 50.0 47.0 | 2900 | 13.6 17.9 19.9 | 22 | Y180M-2 | 65 76 77 | 3.5 3.6 4.8 | 100 | 65 | 86 |
| IS IR100-65-200 IY | 30.0 50.0 60.0 | 8.33 13.89 16.67 | 13.5 12.5 11.8 | 1450 | 1.84 2.33 2.61 | 4 | Y112M-4 | 60 73 74 | 2.0 2.0 2.5 | 100 | 65 | 86 |
| IS IR100-65-200A IY | 57.0 95.0 114.0 | 15.83 26.39 31.67 | 48.7 45.1 42.4 | 2900 | 11.84 15.55 17.28 | 18.5 | Y160L-2 | 64 75 76 | 3.0 3.6 4.8 | 100 | 65 | 86 |
|  | 28.5 47.5 57.0 | 7.92 13.19 15.83 | 12.2 11.3 10.7 | 1450 | 1.16 2.03 2.27 | 3 | Y100L2-4 | 59 72 73 | 2.0 2.0 2.5 |  |  |  |
| IS IR100-65-200B IY | 51.0 85.0 102.0 | 14.17 23.61 28.33 | 39.0 36.1 34.0 | 2900 | 8.62 11.29 12.55 | 15 | Y160M2-2 | 63 74 75 | 2.0 2.0 2.5 | 100 | 65 | 86 |
| IS IR100-65-250 IY | 60.0 100.0 120.0 | 16.67 27.78 33.33 | 87.0 80.0 74.5 | 2900 | 23.4 30.3 33.3 | 37 | Y200L2-2 | 61 72 73 | 3.5 3.8 4.8 | 100 | 65 | 95 |
|  | 30.0 50.0 60.0 | 8.33 13.89 16.67 | 21.3 20.0 19.0 | 1450 | 3.16 4.00 4.44 | 5.5 | Y132S-4 | 55 68 70 | 2.0 2.0 2.5 |  |  |  |
| IS IR100-65-250A IY | 51.0 85.0 102.0 | 14.17 23.61 28.33 | 62.9 57.8 53.8 | 2900 | 14.59 18.87 20.73 | 22 | Y180M-2 | 60 71 72 | 3.5 3.8 4.8 | 100 | 65 | 95 |
|  | 25.5 42.5 51.0 | 7.08 11.81 14.17 | 15.4 14.5 13.7 | 1450 | 1.98 2.50 2.77 | 4 | Y112M-4 | 54 67 69 | 2.0 2.0 2.5 |  |  |  |
| IS IR100-65-250B IY | 48.0 80.0 96.0 | 13.33 22.22 26.67 | 55.68 51.2 47.68 | 2900 | 12.34 15.95 17.57 | 18.5 | Y160L-2 | 59 70 71 | 3.5 3.8 4.8 | 100 | 65 | 95 |
|  | 24.0 40.0 48.0 | 6.67 11.11 13.33 | 13.6 12.8 12.2 | 1450 | 1.68 2.11 2.34 | 3 | Y100L2-4 | 53 66 68 | 2.0 2.0 2.5 |  |  |  |
| IS IR100-65-315 IY | 60.0 100.0 120.0 | 16.67 27.78 33.33 | 133.0 125.0 118.0 | 2900 | 39.6 51.6 57.6 | 75 | Y280S-2 | 55 66 67 | 3.0 3.6 4.2 | 100 | 65 | 130 |
|  | 30.0 50.0 60.0 | 8.33 13.89 16.67 | 34.0 32.0 30.0 | 1450 | 5.45 6.92 7.67 | 11 | Y160M-4 | 51 63 64 | 2.0 2.0 2.5 |  |  |  |
| IS IR100-65-315A IY | 57.0 95.0 114.0 | 15.83 26.39 31.67 | 120.0 112.8 106.5 | 2900 | 34.58 44.92 50.06 | 55 | Y250M-2 | 54 65 66 | 3.0 3.6 4.2 | 100 | 65 | 130 |
|  | 28.5 47.5 57.0 | 7.92 13.19 15.83 | 30.7 28.9 27.1 | 1450 | 4.75 6.03 6.68 | 7.5 | Y132M-4 | 50 62 63 | 2.0 2.0 2.5 |  |  |  |
| IS IR100-65-315B IY | 51.0 85.0 102.0 | 14.17 23.61 28.33 | 96.1 90.3 85.3 | 2900 | 25.24 32.68 36.40 | 45 | Y225M-2 | 53 64 65 | 3.0 3.6 4.2 | 100 | 65 | 130 |
|  | 25.5 42.5 51.0 | 7.08 11.8 14.17 | 24.6 23.1 21.7 | 1450 | 3.48 4.39 4.87 | 5.5 | Y132S-4 | 49 61 62 | 2.0 2.0 2.5 |  |  |  |
| IS IR100-65-315C IY | 48.0 80.0 96.0 | 13.33 22.22 26.67 | 85.1 80.0 75.5 | 2900 | 21.05 27.25 30.35 | 37 | Y200L2-2 | 53 64 65 | 3.0 3.6 4.2 | 100 | 65 | 130 |
| IS IR125-100-200 IY | 120.0 200.0 240.0 | 33.33 55.56 66.67 | 57.5 50.0 44.5 | 2900 | 28.0 33.6 36.4 | 45 | Y225M-2 | 67 81 80 | 4.5 4.5 5.0 | 125 | 100 | 87 |
|  | 60.0 100.0 120.0 | 16.67 27.78 33.33 | 14.5 12.5 11.0 | 1450 | 3.83 4.48 4.80 | 7.5 | Y132M-4 | 62 76 75 | 2.5 2.5 3.0 |  |  |  |
| IS IR125-100-200A IY | 114.0 190.0 228.0 | 31.67 52.78 63.33 | 51.9 45.1 40.2 | 2900 | 24.43 29.19 31.61 | 37 | Y200L2-2 | 66 80 79 | 4.5 4.5 5.0 | 125 | 100 | 87 |
|  | 57.0 95.0 114.0 | 15.83 26.39 31.67 | 13.0 11.3 10.0 | 1450 | 3.31 3.90 4.20 | 5.5 | Y132S-4 | 61 75 74 | 2.5 2.5 3.0 |  |  |  |
| IS IR125-100-200B IY | 96.0 160.0 192.0 | 26.67 44.44 53.33 | 36.8 32.0 28.5 | 2900 | 14.8 17.66 19.12 | 22 | Y180M-2 | 65 79 78 | 4.5 4.5 5.0 | 125 | 100 | 87 |
|  | 48.0 80.0 96.0 | 13.33 22.22 26.67 | 9.3 8.0 7.0 | 1450 | 2.03 2.36 2.51 | 4 | Y112M-4 | 60 74 73 | 2.5 2.5 3.0 |  |  |  |
| IS IR125-100-250 IY | 120.0 200.0 240.0 | 33.33 55.56 66.67 | 87.0 80.0 72.0 | 2900 | 43.1 55.9 62.8 | 75 | Y280S-2 | 66 78 75 | 3.8 4.2 5.0 | 125 | 100 | 115 |
|  | 60.0 100.0 120.0 | 16.67 27.78 33.33 | 21.5 20.0 18.5 | 1450 | 5.58 7.17 7.86 | 11 | Y160M-4 | 63 76 77 | 2.5 2.5 3.0 |  |  |  |
| IS IR125-100-250A IY | 108.0 180.0 216.0 | 30.0 50.0 60.0 | 70.5 64.8 58.3 | 2900 | 31.9 41.28 46.37 | 55 | Y250M-2 | 65 77 74 | 3.8 4.2 5.0 | 125 | 100 | 115 |
|  | 54.0 90.0 108.0 | 15.0 25.0 30.0 | 17.4 16.2 15.0 | 1450 | 4.13 5.30 5.81 | 7.5 | Y132M-4 | 62 75 76 | 2.5 2.5 3.0 |  |  |  |
| IS IR125-100-250B IY | 102.0 170.0 204.0 | 28.33 47.22 56.67 | 62.7 57.8 52.0 | 2900 | 27.24 35.23 39.63 | 45 | Y225M-2 | 64 76 73 | 3.8 4.2 5.0 | 125 | 100 | 115 |
| IS IR125-100-250B IY | 51.0 85.0 102.0 | 14.17 23.61 28.33 | 15.5 14.5 13.4 | 1450 | 3.54 4.52 4.94 | 5.5 | Y132S-4 | 61 74 65 | 2.5 2.5 3.0 | 125 | 100 | 115 |
| IS IR125-100-250C IY | 96.0 160.0 192.0 | 26.67 44.44 53.33 | 55.7 51.2 48.1 | 2900 | 22.71 29.37 33.03 | 37 | Y200L2-2 | 64 76 73 | 3.8 4.2 5.0 | 125 | 100 | 115 |
| IS IR125-100-315 IY | 120.0 200.0 240.0 | 33.33 55.56 66.67 | 132.5 125.0 120.0 | 2900 | 72.1 90.8 101.9 | 110 | Y315S-2 | 60 75 77 | 4.5 4.5 5.0 | 125 | 100 | 125 |
|  | 60.0 100.0 120.0 | 16.67 27.78 33.33 | 33.5 32.0 30.5 | 1450 | 9.4 11.9 13.5 | 15 | Y160L-4 | 58 73 74 | 2.5 2.5 3.0 |  |  |  |
| IS IR125-100-315A IY | 108.0 180.0 216.0 | 30.0 50.0 60.0 | 107.2 101.3 97.2 | 2900 | 53.47 67.15 75.28 | 90 | Y280M-2 | 59 74 76 | 4.0 4.5 5.0 | 125 | 100 | 125 |
|  | 54.0 90.0 108.0 | 15.0 25.0 30.0 | 27.1 25.9 24.7 | 1450 | 7.0 8.82 9.96 | 11 | Y160M-4 | 57 72 73 | 2.5 2.5 3.0 |  |  |  |
| IS IR125-100-315B IY | 102.0 170.0 204.0 | 28.33 47.22 56.67 | 95.7 90.3 86.7 | 2900 | 48.86 57.30 64.27 | 75 | Y280S-2 | 58 73 75 | 4.0 4.5 5.0 | 125 | 100 | 125 |
| IS IR125-100-400 IY | 60.0 100.0 120.0 | 16.67 27.78 33.33 | 52.0 50.0 48.5 | 1450 | 16.1 21.0 23.6 | 30 | Y200L-4 | 53 65 67 | 2.5 2.5 3.0 | 125 | 100 | 137 |
| IS IR125-100-400A IY | 54.0 90.0 108.0 | 15.0 25.0 30.0 | 42.1 40.5 39.3 | 1450 | 11.94 15.52 17.49 | 22 | Y180L-4 | 52 64 66 | 2.5 2.5 3.0 | 125 | 100 | 137 |
| IS IR125-100-400B IY | 51.0 85.0 102.0 | 14.17 23.61 28.33 | 37.6 36.1 35.0 | 1450 | 10.29 13.29 14.96 | 18.5 | Y180M-4 | 51 63 65 | 2.5 2.5 3.0 | 125 | 100 | 137 |
| IS IR125-100-400C IY | 48.0 80.0 96.0 | 13.33 22.22 26.67 | 33.3 32.0 31.0 | 1450 | 8.56 11.09 12.45 | 15 | Y160L-4 | 51 63 65 | 2.5 2.5 3.0 | 125 | 100 | 137 |
| IS IR150-125-250 IY | 120.0 200.0 240.0 | 33.33 55.56 66.67 | 22.5 20.0 17.5 | 1450 | 10.4 13.5 14.7 | 18.5 | Y180M-4 | 71 81 78 | 3.0 3.0 3.5 | 150 | 125 | 136 |
| IS IR150-125-250A IY | 114 190 228 | 31.64 52.82 63.36 | 20.3 18.1 15.8 | 1450 | 9.05 11.71 12.76 | 15 | Y160L-4 | 70 80 77 | 3.0 3.0 3.5 | 150 | 125 | 136 |
| IS IR150-125-250B IY | 102.0 170.0 204.0 | 28.33 47.22 56.67 | 16.3 14.5 12.6 | 1450 | 6.46 8.47 9.25 | 11 | Y160M-4 | 70 79 76 | 3.0 3.0 3.5 | 150 | 125 | 136 |
| IS IR150-125-315 IY | 120.0 200.0 240.0 | 33.33 55.56 66.67 | 34.0 32.0 29.0 | 1450 | 15.86 22.08 23.71 | 30 | Y200L-4 | 70 79 80 | 2.5 2.5 3.0 | 150 | 125 | 158 |
| IS IR150-125-315A IY | 114 190 228 | 31.64 52.78 63.36 | 30.7 28.9 26.2 | 1450 | 13.63 19.17 20.59 | 22 | Y180L-4 | 69 78 79 | 2.5 2.5 3.0 | 150 | 125 | 158 |
| IS IR150-125-315B IY | 105.6 176 211.2 | 29.31 48.93 58.7 | 26.3 24.8 22.5 | 1450 | 11.11.1108 15.44 16.57 | 18.5 | Y180M-4 | 68 77 78 | 2.5 2.5 3.0 | 150 | 125 | 158 |
| IS IR150-125-400 IY | 120 200 240 | 33.33 55.56 66.67 | 53.0 50.0 46.0 | 1450 | 27.9 36.3 40.6 | 45 | Y225M-4 | 62 75 74 | 2.0 2.8 3.5 | 150 | 125 | 187 |
| IS IR150-125-400A IY | 114 190 228 | 31.64 52.82 63.36 | 47.8 45.2 41.5 | 1450 | 24.31 31.54 35.29 | 37 | Y225S-4 | 61 74 73 | 2.0 2.8 3.5 | 150 | 125 | 187 |
| IS IR150-125-400B IY | 105.6 176 211.2 | 29.31 48.93 58.67 | 41.0 38.7 35.6 | 1450 | 19.64 25.42 28.44 | 30 | Y200L-4 | 60 73 72 | 2.0 2.8 3.5 | 150 | 125 | 187 |
| IS IR200-150-250 IY | 240 400 460 | 66.67 111.11 127.78 | 21.5 20.0 17.5 | 1450 | 19.8 26.6 27.4 | 37 | Y225S-4 | 71 82 80 | 3.5 4.3 5.0 | 200 | 150 | 150 |
| IS IR200-150-250A IY | 228 380 437 | 63.37 105.55 121.41 | 19.4 18.1 15.8 | 1450 | 17.2 23.1 23.8 | 30 | Y200L-4 | 70 81 79 | 3.5 4.3 5.0 | 200 | 150 | 150 |
| IS IR200-150-250B IY | 211.2 352 404.8 | 58.67 97.77 112.48 | 16.6 15.5 13.6 | 1450 | 13.8 18.58 19.2 | 22 | Y180L-4 | 69 80 78 | 3.5 4.3 5.0 | 200 | 150 | 150 |
| IS IR200-150-315 IY | 240 400 460 | 66.67 111.11 127.78 | 37 32 28.5 | 1450 | 34.6 42.5 44.6 | 55 | Y250M-4 | 70 82 80 | 3.0 3.5 4.0 | 200 | 150 | 168 |
| IS IR200-150-315A IY | 228 380 437 | 63.37 105.55 121.41 | 33.4 28.9 25.7 | 1450 | 30.1 36.89 38.72 | 45 | 225M-4 | 69 81 79 | 3.0 3.5 4.0 | 200 | 150 | 168 |
| IS IR200-150-315B IY | 211.2 352 404.8 | 58.67 97.77 112.48 | 28.7 24.8 22.1 | 1450 | 24.27 29.68 31.17 | 37 | Y225S-4 | 68 80 78 | 3.0 3.5 4.0 | 200 | 150 | 168 |
| IS IR200-150-315C IY | 204 340 391 | 56.70 94.44 108.63 | 26.7 23.1 20.6 | 1450 | 21.88 26.57 28.09 | 30 | Y200L-4 | 68 80 77 | 3.0 3.5 4.0 | 200 | 150 | 168 |
| IS IR200-150-400 IY | 240 400 460 | 66.67 111.11 127.78 | 55 50 45 | 1450 | 48.6 67.2 74.2 | 90 | Y280M-4 | 74 81 76 | 3.0 3.8 4.5 | 200 | 150 | 186 |
| IS IR200-150-400A IY | 228 380 437 | 63.37 105.55 121.41 | 49.6 45.1 40.6 | 1450 | 42.24 58.34 64.47 | 75 | Y280S-4 | 73 80 75 | 3.0 3.8 4.5 | 200 | 150 | 186 |
| IS IR200-150-400B IY | 211.2 352 404.8 | 58.67 97.77 112.48 | 42.6 38.7 34.9 | 1450 | 34.04 48.95 51.94 | 55 | Y250M-4 | 72 79 74 | 3.0 3.8 4.5 | 200 | 150 | 186 |
| IS IR200-150-400C IY | 192 320 368 | 53.36 88.88 102.24 | 35.2 32.0 28.8 | 1450 | 25.57 35.28 39.02 | 45 | Y225M-4 | 72 79 74 | 3.0 3.8 4.5 | 200 | 150 | 186 |

外形尺寸图

Overall Dimension Drawing

外形尺寸安装图

Overall installing dimension Drawing

| 外形尺寸表 ## Overall Dimension Sheet |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 型 号 Pump Type (IS、IR、IY) | 泵Pump |  |  |  | 泵 脚 座 Foundation |  |  |  |  |  |  |  |  |  |  | w | 螺栓孔 Bolt hole |  | 轴 端 Shaft end |  |
|  | a | f | h1 | h2 | b | m1 | m2 | m3 | m4 | n1 | n2 | n3 | n4 | k1 | k2 |  | s1 | s2 | d | L |
| 50-32-125 | 80 | 385 | 112 | 140 | 50 | 100 | 70 | 19 | 60 | 190 | 140 | 110 | 145 | 14 | 10 | 285 | φ14.5 | φ14.5 | 24 | 50 |
| 50-32-160 |  |  | 132 | 160 |  |  |  |  |  | 240 | 190 |  |  |  |  |  |  |  |  |  |
| 50-32-200 |  |  | 160 | 180 |  |  |  |  |  |  |  |  |  | 16 |  |  |  |  |  |  |
| 50-32-250 | 100 | 500 | 180 | 225 | 65 | 125 | 95 | 25 | 65 | 320 | 250 |  |  | 20 | 14 | 370 |  |  | 32 | 80 |
| 65-50-125 | 80 | 385 | 112 | 140 | 50 | 100 | 70 | 19 | 60 | 210 | 160 | 110 | 145 | 14 | 10 | 285 | φ14.5 | φ14.5 | 24 | 50 |
| 65-50-160 |  |  | 132 | 160 |  |  |  |  |  | 240 | 190 |  |  | 16 |  |  |  |  |  |  |
| 65-40-200 | 100 |  | 160 | 180 |  |  |  |  |  | 265 | 212 |  |  |  |  |  |  |  |  |  |
| 65-40-250 |  | 500 | 180 | 225 | 65 | 125 | 95 | 25 | 65 | 320 | 250 |  |  | 20 | 14 | 370 |  |  | 32 | 80 |
| 65-40-315 | 125 |  | 200 | 250 |  |  |  |  |  | 345 | 280 |  |  |  |  |  |  |  |  |  |
| 80-65-125 | 100 | 385 | 132 | 160 | 50 | 100 | 70 | 19 | 60 | 240 | 190 | 110 | 145 | 16 | 10 | 285 | φ14.5 | φ14.5 | 24 | 50 |
| 80-65-160 |  |  | 160 | 180 |  |  |  |  |  | 265 | 212 |  |  |  |  |  |  |  |  |  |
| 80-50-200 |  |  |  | 200 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 80-50-250 | 125 | 500 | 180 | 225 | 65 | 125 | 95 | 25 | 65 | 320 | 250 |  |  | 20 | 14 | 370 |  |  | 32 | 80 |
| 80-50-315 |  |  | 225 | 280 |  |  |  |  |  | 345 | 280 |  |  |  |  |  |  |  |  |  |
| 100-80-125 | 100 | 385 | 160 | 180 | 65 | 125 | 95 | 19 | 60 | 280 | 212 | 110 | 145 | 16 | 10 | 285 | φ14.5 | φ14.5 | 24 | 50 |
| 100-80-160 |  | 500 |  | 200 |  |  |  | 24 |  |  |  |  |  |  |  | 370 |  |  | 32 | 80 |
| 100-65-200 |  |  | 180 | 255 |  |  |  | 25 | 65 | 320 | 250 |  |  | 20 | 14 |  |  |  |  |  |
| 100-65-250 | 125 |  | 200 | 250 | 80 | 160 | 120 |  |  | 360 | 280 |  |  |  |  |  | φ18.5 |  |  |  |
| 100-65-315 |  | 530 | 225 | 280 |  |  |  | 28 |  | 400 | 315 |  |  | 25 |  |  |  |  | 42 | 110 |
| 125-100-200 | 125 | 500 | 200 | 280 | 80 | 160 | 120 | 25 | 65 | 360 | 280 | 110 | 145 | 20 | 14 | 370 | φ18.5 | φ14.5 | 32 | 80 |
| 125-100-250 | 140 | 530 | 225 |  |  |  |  | 28 |  | 400 | 315 |  |  |  |  |  |  |  | 42 | 110 |
| 125-100-315 |  |  | 250 | 315 |  |  |  |  |  |  |  |  |  | 25 |  |  |  |  |  |  |
| 125-100-400 |  |  | 280 | 355 | 100 | 200 | 150 |  |  | 500 | 400 |  |  |  |  |  | φ24 |  |  |  |
| 150-125-250 | 140 | 530 | 250 | 355 | 80 | 160 | 120 | 28 | 65 | 400 | 315 | 110 | 145 | 25 | 14 | 370 | φ18.5 | φ14.5 | 42 | 110 |
| 150-125-315 |  |  | 280 |  | 100 | 200 | 150 |  |  | 500 | 400 |  |  |  |  |  | φ24 |  |  |  |
| 150-125-400 |  |  | 315 | 400 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 200-150-250 | 160 | 530 | 280 | 370 | 100 | 200 | 150 | 28 | 65 | 500 | 400 | 110 | 145 | 25 | 14 | 370 | φ24 | φ14.5 | 42 | 110 |
| 200-150-315 |  | 670 | 315 | 400 |  |  |  | 38 | 80 | 550 | 450 | 140 | 200 | 30 | 30 | 500 |  | φ18.5 | 48 |  |
| 200-150-400 |  |  |  | 450 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| 外形安装尺寸表 Overall installing dimension sheet |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 泵型号 Pump type (IS、IR、IY) | 配套电机motor |  | A | L1 | L2 | L3 | L4 | L5 | a | f | c | B1 | B2 | B3 | h1 | h2 | h3 | H | H1 | H2 | 4-d |
|  | 型号 type | 功率(KW) power |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 50-32-125 | Y90L-2 | 2.2 | 80 | 790 | 170 | 490 | 335 | 802 | 80 | 385 | 2 | 155 | 390 | 350 | 112 | 190 | 25 | 187 | 327 | 287 | φ18.5 |
|  | Y801-4 | 0.55 | 80 | 750 | 150 | 450 | 285 | 752 | 80 | 385 | 2 | 150 | 360 | 320 | 112 | 170 | 25 | 187 | 327 | 277 | φ18.5 |
| 50-32-125A | Y90S-2 | 1.5 | 80 | 750 | 150 | 450 | 310 | 777 | 80 | 385 | 2 | 155 | 360 | 320 | 112 | 190 | 25 | 187 | 327 | 287 | φ18.5 |
| 50-32-125B | Y802-2 | 1.1 | 80 | 750 | 150 | 450 | 285 | 752 | 80 | 385 | 2 | 150 | 360 | 320 | 112 | 170 | 25 | 187 | 327 | 277 | φ18.5 |
| 50-32-160 | Y100L-2 | 3 | 80 | 790 | 170 | 490 | 380 | 847 | 80 | 385 | 2 | 180 | 390 | 350 | 132 | 245 | 25 | 207 | 367 | 352 | φ18.5 |
|  | Y801-4 | 0.55 | 80 | 750 | 150 | 450 | 285 | 752 | 80 | 385 | 2 | 150 | 360 | 320 | 132 | 170 | 25 | 207 | 367 | 297 | φ18.5 |
| 50-32-160A | Y90L-2 | 2.2 | 80 | 790 | 170 | 490 | 335 | 802 | 80 | 385 | 2 | 155 | 390 | 350 | 132 | 190 | 25 | 207 | 367 | 307 | φ18.5 |
| 50-32-160B | Y90S-2 | 1.5 | 80 | 750 | 150 | 450 | 310 | 777 | 80 | 385 | 2 | 155 | 360 | 320 | 132 | 190 | 25 | 207 | 367 | 307 | φ18.5 |
| 50-32-200 | Y132S1-2 | 5.5 | 80 | 950 | 190 | 570 | 475 | 942 | 80 | 385 | 2 | 210 | 450 | 400 | 160 | 315 | 30 | 235 | 415 | 418 | φ24 |
|  | Y802-4 | 0.75 | 80 | 750 | 150 | 450 | 285 | 752 | 80 | 385 | 2 | 150 | 360 | 320 | 160 | 170 | 25 | 235 | 415 | 325 | φ18.5 |
| 50-32-200A | Y112M-2 | 4 | 80 | 830 | 170 | 490 | 400 | 867 | 80 | 385 | 2 | 190 | 390 | 350 | 160 | 265 | 25 | 235 | 415 | 388 | φ18.5 |
| 50-32-200B | Y100L-2 | 3 | 80 | 830 | 170 | 490 | 380 | 847 | 80 | 385 | 2 | 180 | 390 | 350 | 160 | 245 | 25 | 235 | 415 | 380 | φ18.5 |
| 50-32-250 | Y160M1-2 | 11 | 95 | 1190 | 225 | 740 | 600 | 1202 | 100 | 500 | 2 | 255 | 540 | 490 | 180 | 385 | 30 | 290 | 515 | 515 | φ24 |
|  | Y90L-4 | 1.5 | 95 | 910 | 190 | 570 | 335 | 937 | 100 | 500 | 2 | 155 | 450 | 400 | 180 | 190 | 30 | 255 | 480 | 355 | φ24 |
| 50-32-250A | Y132S2-2 | 7.5 | 95 | 1050 | 210 | 630 | 475 | 1077 | 100 | 500 | 2 | 210 | 490 | 440 | 180 | 315 | 30 | 270 | 495 | 453 | φ24 |
|  | Y90S-4 | 1.1 | 95 | 910 | 190 | 570 | 310 | 912 | 100 | 500 | 2 | 155 | 450 | 400 | 180 | 190 | 30 | 255 | 480 | 355 | φ24 |
| 65-50-125 | Y100L-2 | 3 | 80 | 830 | 170 | 490 | 380 | 847 | 80 | 385 | 2 | 180 | 390 | 350 | 112 | 245 | 25 | 187 | 327 | 332 | φ18.5 |
|  | Y801-4 | 0.55 | 80 | 750 | 150 | 450 | 285 | 752 | 80 | 385 | 2 | 150 | 360 | 320 | 112 | 170 | 25 | 187 | 327 | 277 | φ18.5 |
| 65-50-125A | Y90L-2 | 2.2 | 80 | 790 | 170 | 490 | 335 | 802 | 80 | 385 | 2 | 155 | 390 | 350 | 112 | 190 | 25 | 187 | 327 | 287 | φ18.5 |
| 65-50-125B | Y90S-2 | 1.5 | 80 | 750 | 150 | 450 | 310 | 777 | 80 | 385 | 2 | 155 | 360 | 320 | 112 | 190 | 25 | 187 | 327 | 287 | φ18.5 |
| 65-50-160 | Y132S1-2 | 5.5 | 80 | 910 | 190 | 570 | 475 | 942 | 80 | 385 | 2 | 210 | 450 | 400 | 132 | 315 | 30 | 207 | 367 | 390 | φ24 |
|  | Y802-4 | 0.75 | 80 | 750 | 150 | 450 | 285 | 752 | 80 | 385 | 2 | 150 | 360 | 320 | 132 | 170 | 25 | 207 | 367 | 297 | φ18.5 |
| 65-50-160A | Y112M-2 | 4 | 80 | 830 | 170 | 490 | 400 | 867 | 80 | 385 | 2 | 190 | 390 | 350 | 132 | 265 | 25 | 207 | 367 | 360 | φ18.5 |
| 65-50-160B | Y100L-2 | 3 | 80 | 830 | 170 | 490 | 380 | 847 | 80 | 385 | 2 | 180 | 390 | 350 | 132 | 245 | 25 | 207 | 367 | 352 | φ18.5 |
| 65-40-200 | Y132S2-2 | 7.5 | 80 | 950 | 190 | 570 | 475 | 962 | 100 | 385 | 2 | 210 | 450 | 400 | 160 | 315 | 30 | 235 | 415 | 418 | φ24 |
|  | Y90S-4 | 1.1 | 80 | 790 | 170 | 490 | 310 | 797 | 100 | 385 | 2 | 155 | 390 | 350 | 160 | 190 | 25 | 235 | 415 | 335 | φ18.5 |
| 65-40-200A | Y112M-2 | 4 | 80 | 830 | 170 | 490 | 400 | 887 | 100 | 385 | 2 | 190 | 390 | 350 | 160 | 265 | 25 | 235 | 415 | 388 | φ18.5 |
|  | Y802-4 | 0.75 | 80 | 790 | 170 | 490 | 285 | 772 | 100 | 385 | 2 | 150 | 390 | 350 | 160 | 170 | 25 | 235 | 415 | 325 | φ18.5 |
| 65-40-250 | Y160M2-2 | 15 | 95 | 1190 | 225 | 740 | 600 | 1182 | 100 | 500 | 2 | 255 | 540 | 490 | 180 | 385 | 30 | 290 | 515 | 515 | φ24 |
|  | Y100L-4 | 2.2 | 95 | 950 | 190 | 570 | 380 | 982 | 100 | 500 | 2 | 180 | 450 | 400 | 180 | 245 | 30 | 255 | 480 | 400 | φ24 |
| 65-40-250A | Y132S2-2 | 7.5 | 95 | 1050 | 210 | 630 | 475 | 1057 | 100 | 500 | 2 | 210 | 490 | 440 | 180 | 315 | 30 | 270 | 495 | 453 | φ24 |
|  | Y90L-4 | 1.5 | 95 | 910 | 190 | 570 | 335 | 937 | 100 | 500 | 2 | 155 | 450 | 400 | 180 | 190 | 30 | 255 | 480 | 355 | φ24 |
| 65-40-315 | Y200L1-2 | 30 | 95 | 1290 | 250 | 830 | 775 | 1402 | 125 | 500 | 2 | 310 | 610 | 550 | 200 | 475 | 40 | 330 | 580 | 605 | φ28 |
|  | Y112M-4 | 4 | 95 | 910 | 210 | 630 | 400 | 1027 | 125 | 500 | 2 | 190 | 490 | 440 | 200 | 265 | 30 | 290 | 540 | 443 | φ24 |
| 65-40-315A | Y180M-2 | 22 | 95 | 1190 | 225 | 740 | 670 | 1297 | 125 | 500 | 2 | 285 | 540 | 490 | 200 | 430 | 30 | 310 | 560 | 560 | φ24 |
|  | Y100L-4 | 3 | 95 | 910 | 210 | 630 | 380 | 1007 | 125 | 500 | 2 | 180 | 490 | 440 | 200 | 245 | 30 | 290 | 540 | 435 | φ24 |
| 65-40-315B | Y160L-2 | 18.5 | 95 | 1190 | 225 | 740 | 645 | 1272 | 125 | 500 | 2 | 255 | 540 | 490 | 200 | 385 | 30 | 310 | 560 | 535 | φ24 |
| 80-65-125 | Y132S-2 | 5.5 | 80 | 910 | 190 | 570 | 475 | 962 | 100 | 385 | 2 | 210 | 450 | 400 | 132 | 315 | 30 | 207 | 367 | 390 | φ24 |
|  | Y802-4 | 0.75 | 80 | 750 | 150 | 450 | 285 | 772 | 100 | 385 | 2 | 150 | 360 | 320 | 132 | 170 | 25 | 207 | 367 | 297 | φ18.5 |
| 80-65-125A | Y112M-2 | 4 | 80 | 830 | 170 | 490 | 400 | 887 | 100 | 385 | 2 | 190 | 390 | 350 | 132 | 265 | 25 | 207 | 367 | 360 | φ18.5 |
| 80-65-125B | Y100L-2 | 3 | 80 | 830 | 170 | 490 | 380 | 867 | 100 | 385 | 2 | 180 | 390 | 350 | 132 | 245 | 25 | 207 | 367 | 352 | φ18.5 |
| 80-65-160 | Y132S2-2 | 7.5 | 80 | 950 | 190 | 570 | 475 | 962 | 100 | 385 | 2 | 210 | 450 | 400 | 160 | 315 | 30 | 235 | 415 | 418 | φ24 |
|  | Y90L-4 | 1.5 | 80 | 790 | 170 | 490 | 335 | 822 | 100 | 385 | 2 | 155 | 390 | 350 | 160 | 190 | 25 | 235 | 415 | 334 | φ18.5 |
| 80-65-160A | Y112M-2 | 4 | 80 | 830 | 170 | 490 | 400 | 887 | 100 | 385 | 2 | 190 | 390 | 350 | 160 | 265 | 25 | 235 | 415 | 388 | φ18.5 |
|  | Y90S-4 | 1.1 | 80 | 790 | 170 | 490 | 310 | 797 | 100 | 385 | 2 | 155 | 390 | 350 | 160 | 190 | 25 | 235 | 415 | 335 | φ18.5 |
| 80-50-200 | Y160M2-2 | 15 | 80 | 1050 | 210 | 630 | 600 | 1087 | 100 | 385 | 2 | 255 | 490 | 440 | 160 | 385 | 30 | 250 | 450 | 475 | φ24 |
|  | Y100L-4 | 2.2 | 80 | 830 | 170 | 490 | 380 | 867 | 100 | 385 | 2 | 180 | 390 | 350 | 160 | 245 | 25 | 235 | 435 | 380 | φ18.5 |
| 80-50-200A | Y132S2-2 | 7.5 | 80 | 950 | 190 | 570 | 475 | 962 | 100 | 385 | 2 | 210 | 450 | 400 | 160 | 315 | 30 | 235 | 435 | 418 | φ24 |
| 80-50-200A | Y90L-4 | 1.5 | 80 | 790 | 170 | 490 | 335 | 822 | 100 | 385 | 2 | 155 | 390 | 350 | 160 | 190 | 25 | 235 | 435 | 335 | φ18.5 |
| 80-50-200B | Y132S2-2 | 7.5 | 80 | 950 | 190 | 570 | 475 | 962 | 100 | 385 | 2 | 210 | 450 | 400 | 160 | 315 | 30 | 235 | 435 | 418 | φ24 |
|  | Y90S-4 | 1.1 | 80 | 790 | 170 | 490 | 310 | 797 | 100 | 385 | 2 | 155 | 390 | 350 | 160 | 190 | 25 | 235 | 435 | 335 | φ18.5 |
| 80-50-250 | Y180M-2 | 22 | 95 | 1190 | 225 | 740 | 670 | 1297 | 125 | 500 | 2 | 285 | 540 | 490 | 180 | 430 | 30 | 290 | 515 | 540 | φ24 |
|  | Y100L-4 | 3 | 95 | 950 | 190 | 570 | 380 | 1007 | 125 | 500 | 2 | 180 | 450 | 400 | 180 | 245 | 30 | 255 | 480 | 400 | φ24 |
| 80-50-250A | Y160L-2 | 18.5 | 95 | 1190 | 225 | 740 | 645 | 1272 | 125 | 500 | 2 | 255 | 540 | 490 | 180 | 385 | 30 | 290 | 515 | 515 | φ24 |
| 80-50-250B | Y160M2-2 | 15 | 95 | 1190 | 225 | 740 | 600 | 1227 | 125 | 500 | 2 | 255 | 540 | 490 | 180 | 385 | 30 | 290 | 515 | 515 | φ24 |
| 80-50-315 | Y200L2-2 | 37 | 95 | 1290 | 250 | 830 | 775 | 1402 | 125 | 500 | 2 | 310 | 610 | 550 | 225 | 475 | 40 | 335 | 635 | 630 | φ28 |
|  | Y132S-4 | 5.5 | 95 | 1050 | 210 | 630 | 475 | 1102 | 125 | 500 | 2 | 210 | 490 | 440 | 225 | 315 | 30 | 315 | 595 | 498 | φ24 |
| 80-50-315A | Y180M-2 | 22 | 95 | 1190 | 225 | 740 | 670 | 1297 | 125 | 500 | 2 | 285 | 540 | 490 | 225 | 430 | 30 | 335 | 615 | 585 | φ24 |
|  | Y112M-4 | 4 | 95 | 970 | 210 | 630 | 400 | 1027 | 125 | 500 | 2 | 190 | 490 | 440 | 225 | 265 | 30 | 315 | 595 | 468 | φ24 |
| 100-80-125 | Y160M1-2 | 11 | 95 | 1050 | 210 | 630 | 600 | 1087 | 100 | 385 | 2 | 255 | 490 | 440 | 160 | 385 | 30 | 250 | 430 | 475 | φ24 |
|  | Y90L-4 | 1.5 | 95 | 790 | 170 | 490 | 335 | 822 | 100 | 385 | 2 | 155 | 390 | 350 | 160 | 190 | 25 | 235 | 415 | 335 | φ18.5 |
| 100-80-125A | Y132S2-2 | 7.5 | 95 | 950 | 190 | 570 | 475 | 962 | 100 | 385 | 2 | 210 | 450 | 400 | 160 | 315 | 30 | 235 | 415 | 418 | φ24 |
|  | Y90S-4 | 1.1 | 95 | 790 | 170 | 490 | 310 | 797 | 100 | 385 | 2 | 155 | 390 | 350 | 160 | 190 | 25 | 235 | 415 | 335 | φ18.5 |
| 100-80-125B | Y132S-2 | 5.5 | 95 | 950 | 190 | 570 | 475 | 962 | 100 | 385 | 2 | 210 | 450 | 400 | 160 | 315 | 30 | 235 | 415 | 335 | φ18.5 |
| 100-80-125B | Y802-4 | 0.75 | 95 | 790 | 170 | 490 | 285 | 772 | 100 | 385 | 2 | 150 | 390 | 350 | 160 | 170 | 25 | 235 | 415 | 325 | φ18.5 |
| 100-80-160 | Y160M2-2 | 15 | 95 | 1100 | 225 | 740 | 600 | 1202 | 100 | 500 | 2 | 255 | 540 | 490 | 160 | 385 | 30 | 270 | 470 | 495 | φ24 |
|  | Y100L-4 | 2.2 | 95 | 950 | 190 | 570 | 380 | 982 | 100 | 500 | 2 | 180 | 450 | 400 | 160 | 245 | 30 | 235 | 435 | 380 | φ24 |
| 100-80-160A | Y160M1-2 | 11 | 95 | 1190 | 225 | 740 | 600 | 1202 | 100 | 500 | 2 | 255 | 540 | 490 | 160 | 385 | 30 | 270 | 470 | 495 | φ24 |
|  | Y90L-4 | 1.5 | 95 | 910 | 190 | 570 | 335 | 937 | 100 | 500 | 2 | 155 | 450 | 400 | 160 | 190 | 30 | 235 | 435 | 335 | φ24 |
| 100-65-200 | Y180M-2 | 22 | 95 | 1190 | 225 | 740 | 670 | 1272 | 100 | 500 | 2 | 285 | 540 | 490 | 180 | 430 | 30 | 290 | 515 | 540 | φ24 |
|  | Y112M-4 | 4 | 95 | 970 | 210 | 630 | 400 | 1002 | 100 | 500 | 2 | 190 | 490 | 440 | 180 | 265 | 30 | 270 | 495 | 423 | φ24 |
| 100-65-200A | Y160L-2 | 18.5 | 95 | 1190 | 225 | 740 | 645 | 1247 | 100 | 500 | 2 | 255 | 540 | 490 | 180 | 385 | 30 | 290 | 515 | 515 | φ24 |
|  | Y100L2-4 | 3 | 95 | 970 | 210 | 630 | 380 | 982 | 100 | 500 | 2 | 180 | 490 | 440 | 180 | 245 | 30 | 270 | 495 | 415 | φ24 |
| 100-65-200B | Y160M2-2 | 15 | 95 | 1190 | 225 | 740 | 600 | 1202 | 100 | 500 | 2 | 255 | 540 | 490 | 180 | 385 | 30 | 290 | 515 | 515 | φ24 |
| 100-65-250 | Y200L2-2 | 37 | 110 | 1290 | 250 | 830 | 775 | 1402 | 125 | 500 | 2 | 310 | 610 | 550 | 200 | 475 | 40 | 330 | 580 | 605 | φ28 |
|  | Y132S-4 | 5.5 | 110 | 1050 | 210 | 630 | 475 | 1102 | 125 | 500 | 2 | 210 | 490 | 440 | 200 | 315 | 30 | 290 | 540 | 473 | φ24 |
| 100-65-250A | Y180M-2 | 22 | 110 | 1190 | 225 | 740 | 670 | 1297 | 125 | 500 | 2 | 285 | 540 | 490 | 200 | 430 | 30 | 310 | 560 | 560 | φ24 |
|  | Y112M-4 | 4 | 110 | 970 | 210 | 630 | 400 | 1027 | 125 | 500 | 2 | 190 | 490 | 440 | 200 | 265 | 30 | 290 | 540 | 443 | φ24 |
| 100-65-250B | Y160L-2 | 18.5 | 110 | 1190 | 225 | 740 | 645 | 1272 | 125 | 500 | 2 | 265 | 540 | 490 | 200 | 385 | 30 | 310 | 560 | 535 | φ24 |
|  | Y100L2-4 | 3 | 110 | 970 | 210 | 630 | 380 | 1007 | 125 | 500 | 2 | 180 | 490 | 440 | 200 | 245 | 30 | 290 | 540 | 435 | φ24 |
| 100-65-315 | Y280S-2 | 75 | 110 | 1590 | 320 | 1070 | 1000 | 1657 | 125 | 530 | 2 | 410 | 730 | 670 | 225 | 640 | 40 | 425 | 705 | 785 | φ28 |
|  | Y160M-4 | 11 | 110 | 1190 | 225 | 740 | 600 | 1257 | 125 | 530 | 2 | 255 | 540 | 490 | 225 | 385 | 30 | 335 | 615 | 560 | φ24 |
| 100-65-315A | Y250M-2 | 55 | 110 | 1450 | 290 | 870 | 930 | 1587 | 125 | 530 | 2 | 385 | 660 | 600 | 225 | 575 | 40 | 425 | 705 | 750 | φ28 |
|  | Y132M-4 | 7.5 | 110 | 1100 | 225 | 740 | 515 | 1172 | 125 | 530 | 2 | 210 | 540 | 490 | 225 | 315 | 30 | 335 | 615 | 518 | φ24 |
| 100-65-315B | Y225M-2 | 45 | 110 | 1450 | 290 | 870 | 815 | 1472 | 125 | 530 | 2 | 345 | 660 | 600 | 225 | 530 | 40 | 375 | 655 | 680 | φ28 |
|  | Y132S-4 | 5.5 | 110 | 1190 | 225 | 740 | 475 | 1132 | 125 | 530 | 2 | 210 | 540 | 490 | 225 | 315 | 30 | 335 | 615 | 518 | φ24 |
| 100-65-315C | Y200L2-2 | 37 | 110 | 1290 | 250 | 830 | 775 | 1432 | 125 | 530 | 2 | 310 | 610 | 550 | 225 | 475 | 40 | 355 | 635 | 630 | φ28 |
| 125-100-200 | Y225M-2 | 45 | 110 | 1290 | 250 | 830 | 815 | 1442 | 125 | 500 | 2 | 345 | 610 | 550 | 200 | 530 | 40 | 360 | 640 | 665 | φ28 |
|  | Y132M-4 | 7.5 | 110 | 1050 | 210 | 630 | 515 | 1142 | 125 | 500 | 2 | 210 | 490 | 440 | 200 | 315 | 30 | 290 | 570 | 473 | φ24 |
| 125-100-200A | Y200L2-2 | 37 | 110 | 1290 | 250 | 830 | 775 | 1402 | 125 | 500 | 2 | 310 | 610 | 550 | 200 | 475 | 40 | 330 | 610 | 605 | φ28 |
|  | Y132S-4 | 5.5 | 110 | 1050 | 210 | 630 | 475 | 1102 | 125 | 500 | 2 | 210 | 490 | 440 | 200 | 315 | 30 | 290 | 570 | 473 | φ24 |
| 125-100-200B | Y180M-2 | 22 | 110 | 1190 | 225 | 740 | 670 | 1297 | 125 | 500 | 2 | 285 | 540 | 490 | 200 | 430 | 30 | 310 | 590 | 560 | φ24 |
| 125-100-200B | Y112M-4 | 4 | 110 | 970 | 210 | 630 | 400 | 1027 | 125 | 500 | 2 | 190 | 490 | 440 | 200 | 265 | 30 | 290 | 570 | 443 | φ24 |
| 125-100-250 | Y280S-2 | 75 | 110 | 1590 | 320 | 1070 | 1000 | 1672 | 140 | 530 | 2 | 410 | 730 | 670 | 225 | 640 | 40 | 425 | 705 | 785 | Φ28 |
|  | Y160M-4 | 11 | 110 | 1190 | 225 | 740 | 600 | 1272 | 140 | 530 | 2 | 255 | 540 | 490 | 225 | 385 | 30 | 335 | 615 | 560 | φ28 |
| 125-100-250A | Y250M-2 | 55 | 110 | 1450 | 290 | 870 | 930 | 1602 | 140 | 530 | 2 | 385 | 660 | 600 | 225 | 575 | 40 | 425 | 705 | 750 | φ28 |
| 125-100-250A | Y132M-4 | 7.5 | 110 | 1100 | 225 | 740 | 515 | 1187 | 140 | 530 | 2 | 210 | 540 | 490 | 225 | 315 | 30 | 335 | 615 | 518 | φ28 |
| 125-100-250B | Y225M-2 | 45 | 110 | 1450 | 290 | 870 | 815 | 1487 | 140 | 530 | 2 | 345 | 660 | 600 | 225 | 530 | 40 | 375 | 655 | 680 | φ28 |
|  | Y132S-4 | 5.5 | 110 | 1100 | 225 | 740 | 475 | 1147 | 140 | 530 | 2 | 210 | 540 | 490 | 225 | 315 | 30 | 335 | 615 | 518 | φ28 |
| 125-100-250C | Y200L2-2 | 37 | 110 | 1290 | 250 | 830 | 775 | 1447 | 140 | 530 | 2 | 310 | 610 | 550 | 225 | 475 | 40 | 355 | 635 | 630 | φ28 |
| 125-100-315 | Y315S-2 | 110 | 110 | 1630 | 320 | 1070 | 1190 | 1863 | 140 | 530 | 3 | 460 | 800 | 740 | 250 | 760 | 40 | 450 | 765 | 895 | φ28 |
|  | Y160L-4 | 15 | 110 | 1240 | 250 | 830 | 645 | 1317 | 140 | 530 | 2 | 225 | 610 | 550 | 250 | 385 | 40 | 380 | 695 | 605 | φ28 |
| 125-100-315A | Y280M-2 | 90 | 110 | 1590 | 320 | 1070 | 1050 | 1723 | 140 | 530 | 3 | 410 | 730 | 670 | 250 | 640 | 40 | 450 | 765 | 810 | φ28 |
|  | Y160M-4 | 11 | 110 | 1190 | 225 | 740 | 600 | 1272 | 140 | 530 | 2 | 225 | 540 | 490 | 250 | 385 | 30 | 360 | 675 | 585 | φ24 |
| 125-100-315B | Y280S-2 | 75 | 110 | 1590 | 320 | 1070 | 1000 | 1673 | 140 | 530 | 3 | 410 | 730 | 670 | 250 | 640 | 40 | 450 | 765 | 810 | φ28 |
| 125-100-400 | Y200L-4 | 30 | 130 | 1320 | 290 | 870 | 775 | 1447 | 140 | 530 | 2 | 310 | 660 | 600 | 280 | 475 | 40 | 430 | 785 | 705 | φ28 |
| 125-100-400A | Y180L-4 | 22 | 130 | 1320 | 290 | 870 | 710 | 1382 | 140 | 530 | 2 | 285 | 660 | 600 | 280 | 430 | 40 | 430 | 785 | 680 | φ28 |
| 125-100-400B | Y180M-4 | 18.5 | 130 | 1320 | 290 | 870 | 670 | 1342 | 140 | 530 | 2 | 285 | 660 | 600 | 280 | 430 | 40 | 430 | 785 | 680 | φ28 |
| 125-100-400C | Y160L-4 | 15 | 130 | 1320 | 290 | 870 | 645 | 1317 | 140 | 530 | 2 | 255 | 660 | 600 | 280 | 385 | 40 | 430 | 785 | 655 | φ28 |
| 150-125-250 | Y180M-4 | 18.5 | 110 | 1240 | 250 | 830 | 670 | 1342 | 140 | 530 | 2 | 285 | 610 | 550 | 250 | 430 | 40 | 380 | 735 | 630 | φ28 |
| 150-125-250A | Y160L-4 | 15 | 110 | 1240 | 250 | 830 | 645 | 1317 | 140 | 530 | 2 | 255 | 610 | 550 | 250 | 385 | 40 | 380 | 735 | 605 | φ28 |
| 150-125-250B | Y160M-4 | 11 | 110 | 1190 | 225 | 740 | 600 | 1272 | 140 | 530 | 2 | 255 | 540 | 490 | 250 | 385 | 30 | 360 | 715 | 585 | φ24 |
| 150-125-315 | Y200L-4 | 30 | 130 | 1320 | 290 | 870 | 775 | 1447 | 140 | 530 | 2 | 310 | 660 | 600 | 280 | 475 | 40 | 430 | 785 | 705 | φ28 |
| 150-125-315A | Y180L-4 | 22 | 130 | 1320 | 290 | 870 | 710 | 1382 | 140 | 530 | 2 | 285 | 660 | 600 | 280 | 430 | 40 | 430 | 785 | 680 | φ28 |
| 150-125-315B | Y180M-4 | 18.5 | 130 | 1320 | 290 | 870 | 670 | 1342 | 140 | 530 | 2 | 285 | 660 | 600 | 280 | 430 | 40 | 430 | 785 | 680 | φ28 |
| 150-125-400 | Y225M-4 | 45 | 130 | 1450 | 290 | 870 | 845 | 1518 | 140 | 530 | 3 | 345 | 660 | 600 | 315 | 530 | 40 | 465 | 865 | 770 | φ28 |
| 150-125-400A | Y225S-4 | 37 | 130 | 1450 | 290 | 870 | 820 | 1493 | 140 | 530 | 3 | 345 | 660 | 600 | 315 | 530 | 40 | 465 | 865 | 770 | φ28 |
| 150-125-400B | Y200L-4 | 30 | 130 | 1320 | 290 | 870 | 775 | 1447 | 140 | 530 | 2 | 310 | 660 | 600 | 315 | 475 | 40 | 465 | 865 | 740 | φ28 |
| 200-150-250 | Y225S-4 | 37 | 130 | 1450 | 290 | 870 | 820 | 1492 | 140 | 530 | 2 | 345 | 660 | 600 | 280 | 530 | 40 | 430 | 805 | 735 | φ28 |
| 200-150-250A | Y200L-4 | 30 | 130 | 1320 | 290 | 870 | 775 | 1467 | 160 | 530 | 2 | 310 | 660 | 600 | 280 | 475 | 40 | 430 | 805 | 705 | φ28 |
| 200-150-250B | Y180L-4 | 22 | 130 | 1320 | 290 | 870 | 710 | 1402 | 160 | 530 | 2 | 285 | 660 | 600 | 280 | 430 | 40 | 430 | 805 | 680 | φ28 |
| 200-150-315 | Y250M-4 | 55 | 130 | 1590 | 320 | 1070 | 930 | 1763 | 160 | 670 | 3 | 385 | 730 | 670 | 315 | 575 | 40 | 465 | 865 | 790 | φ28 |
| 200-150-315A | Y225M-4 | 45 | 130 | 1590 | 320 | 1070 | 845 | 1677 | 160 | 670 | 3 | 345 | 730 | 670 | 315 | 530 | 40 | 465 | 865 | 770 | φ28 |
| 200-150-315B | Y225S-4 | 37 | 130 | 1590 | 320 | 1070 | 820 | 1652 | 160 | 670 | 3 | 345 | 730 | 670 | 315 | 530 | 40 | 465 | 865 | 770 | φ28 |
| 200-150-315C | Y200L-4 | 30 | 130 | 1590 | 320 | 1070 | 775 | 1607 | 160 | 670 | 2 | 310 | 730 | 670 | 315 | 475 | 40 | 465 | 865 | 740 | φ28 |
| 200-150-400 | Y280M-4 | 90 | 130 | 1710 | 320 | 1070 | 1050 | 1883 | 160 | 670 | 3 | 410 | 730 | 670 | 315 | 640 | 40 | 465 | 915 | 825 | φ28 |
| 200-150-400A | Y280S-4 | 75 | 130 | 1710 | 320 | 1070 | 1000 | 1883 | 160 | 670 | 3 | 410 | 730 | 670 | 315 | 640 | 40 | 465 | 915 | 825 | φ28 |
| 200-150-400B | Y250M-4 | 55 | 130 | 1590 | 320 | 1070 | 930 | 1763 | 160 | 670 | 3 | 385 | 730 | 670 | 315 | 575 | 40 | 465 | 915 | 790 | φ28 |
| 200-150-400C | Y225M-4 | 45 | 130 | 1590 | 320 | 1070 | 845 | 1677 | 160 | 670 | 3 | 345 | 730 | 670 | 315 | 530 | 40 | 465 | 915 | 770 | φ28 |

法兰尺寸图

Flange Dimension Drawing

法兰尺寸表

Flange Dimension Sheet

| 泵型号 Pump type |  | 吸入口法兰尺寸(mm)` suction flange dimension |  |  |  |  |  |  | 排出口法兰尺寸(mm) discharge flange dimension |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | DN1 | D1 | D11 | d1 | b1 | f1 | n1-d01 | DN2 | D2 | D12 | d2 | b2 | f2 | n2-d02 |
| IS IR IY | 50-32-125 | 50 | 165 | 125 | 102 | 20 | 3 | 4-φ17.5 | 32 | 140 | 100 | 78 | 18 | 2 | 4-φ17.5 |
|  | 50-32-160 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 50-32-200 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 50-32-250 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 65-50-125 | 65 | 185 | 145 | 122 | 20 | 3 | 4-φ17.5 | 50 | 165 | 125 | 102 | 20 | 3 | 4-φ17.5 |
|  | 65-50-160 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 65-40-200 |  |  |  |  |  |  |  | 40 | 150 | 110 | 88 | 18 | 3 | 4-φ17.5 |
|  | 65-40-250 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 65-40-315 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 80-65-125 | 80 | 200 | 160 | 133 | 22 | 3 | 8-φ17.5 | 65 | 185 | 145 | 122 | 20 | 3 | 4-φ17.5 |
|  | 80-65-160 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 80-50-200 |  |  |  |  |  |  |  | 50 | 165 | 125 | 102 | 20 | 3 | 4-φ17.5 |
|  | 80-50-250 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 80-50-315 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 100-80-125 | 100 | 220 | 180 | 158 | 24 | 3 | 8-φ17.5 | 80 | 200 | 160 | 133 | 22 | 3 | 8-φ17.5 |
|  | 100-80-160 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 100-65-200 |  |  |  |  |  |  |  | 65 | 185 | 145 | 122 | 20 | 3 | 4-φ17.5 |
|  | 100-65-250 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 100-65-315 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 125-100-200 | 125 | 250 | 210 | 184 | 26 | 3 | 8-φ17.5 | 100 | 220 | 180 | 158 | 24 | 3 | 8-φ17.5 |
|  | 125-100-250 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 125-100-315 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 125-100-400 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 150-125-250 | 150 | 285 | 240 | 212 | 26 | 3 | 8-φ22 | 125 | 250 | 210 | 184 | 26 | 3 | 8-φ17.5 |
|  | 150-125-315 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 150-125-400 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 200-150-250 | 200 | 340 | 295 | 268 | 30 | 3 | 12-φ22 | 150 | 285 | 240 | 212 | 26 | 3 | 8-φ22 |
|  | 200-150-315 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 200-150-400 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

装配与拆卸

泵在装配前，应当首先检查零件有无影响装配的缺陷，并擦洗干净，方可进行装配。

- 预先可将各处的连接螺栓、丝堵等分别拧紧在相应的零件上。

- 预先可将O型密封圈、纸垫、毛毡等分别放置在相应的零件上。

- 预先可将密封环和填料、填料环、填料压盖等依次装到泵盖内。

- 将滚动轴承装到轴上，然后装到悬架内，再合上压盖，压紧滚动轴承，并在轴上套上挡水圈。

- 将轴套装到轴上，再将泵盖装到悬架上，然后再将叶轮、止动垫圈、叶轮螺母等装上并拧紧。最后将上述组件装到泵体内，并拧紧泵体、泵盖上的连接螺栓。

在上述装配过程中，一些小件如平键、挡油盘、挡水圈、轴套内O型密封圈等容易遗漏或装错顺序，应特别注意。

泵拆卸顺序基本上可按装配顺序的反向进行。

Assembly and Disassembly

Before assembly, the all parts should be checked, ensure these parts in good condition, and wipe up cleanly, then assembly.

- Tighten the blots, pins in relative parts respectively.

- Place the “O” ring, paper gasket, gaskets on the relative parts.

- Place wearing, packing, packing ring, packing cover on the pump cover orderly.

- Mount the roll bearing in shaft, then assemble them in cantilever support, cover the pump cover, tighten the roll bearing, mount blocking water ring on the shaft.

- Mount the sleeve on the shaft, assemble the pump cover on the cantilever then assemble impeller, gasket, impeller nut etc. and tighten them. Last assemble these parts in pump casing, and tighten bolts on pump casing and pump cover.

In the state process, the small parts, for example, key, blocking oil disc; blocking water ring and “O” ring are easily lose or assemble wrong in orderly.

So these parts assemble should be cared specially.

Disassembly is according to the opposite order of assembly.

安装

泵安装的好坏对泵的运行和寿命有重要影响，所以安装和校正必须仔细进行。

- 安装和校正

- 消除底座上的油腻污垢，把底座放在地基上；

- 用水平仪检查底座的水平度，允许楔铁找平；

- 用水泥浇灌底座和地脚螺栓孔眼。（底座的地脚螺栓一般留预留孔，采用二次灌浆埋设）

- 水泥干固后应检查底座和地脚螺栓是否松动，合适后拧紧地脚螺栓配套螺母，重新检查水平度。

- 清理底座的支撑平面、水泵脚及电机脚的平面，并把水泵和电机安装到底座上。

- 联轴器之间应保持一定的间隙，检查水泵轴与电机轴中心线是否一致，可用薄垫片调整使其同心。

测量联轴器的外圆，使其上、下、左、右的差别不得超过0.1mm。

两联轴器端面间隙一周范围内最大和最小的间隙差别不得超过0.3mm，名义间隙2~3mm。

- 安装说明

- 泵的安装高度，管路的长度、直径、流速应符合计算，力求减少不必要的损失。

- 长距离输送时应取较大的管径。泵的管路应有自己的支架，不允许管路的重量加在泵上，避免把泵压坏。

- 排出管路如装逆止阀，一般装在闸阀和泵出口之间。

- 如采用IR型泵输送温度较高的液体时，须在泵盖上接冷却水和体外水封管。

installing

Pump installing quality is effected directly on pump running and life. So installing and adjusting must be strict.

- Installing and adjusting

(1). Clean the base, then place the base on foundation.

(2). Check the base level degree, permit to level the base by wedge.

(3). Pour concrete into foundation and foundation bolt hole. (Foundation usually have ready hole, adopt second pouring to fill in.)

(4). After the grout is hard, check and ensure the base and foundation tight. Tighten foundation nuts, check the level degree again.

(5). Clean the base support surface, pump foot and motor foot surface, install the pump and motor on the base.

(6). Between coupling halves should have required clearance, check the center line of pump shaft and motor shaft, can adopt thin gaskets to adjust it.

Measure coupling outer circle, the tolerance is not more than 0.1mm.

Max. clearance and min clearance tolerance between the coupling is not more than 0.3mm. nominal clearance is 2-3mm.

- Installing Description

(1). Pump installing height, pipe length, diameter, and flow velocity should satisfied requirement. Reduce unnecessary loss.

(2). If the delivering distance is long, the pipe should be adopted bigger pipe diameter, pipe should have separate support, pump do not allow bear pipe weight.

(3). If the discharge pipe have check valve, the check valve should install between pump discharge and fate valve.

(4). When IR pump deliver high temperature liquid, on the pump cover the cooling water and outer water pipe must be installed.

起动、停止和运行

- 起动

- 应在机泵联接前确定电动机的旋转方向是否正确，泵的转动是否灵活。向悬架内加润滑油，油位应在油镜的中线位置。

- 关闭吐出管路上的闸阀。

- 向泵内灌满水，或用真空泵引水。

- 接通电源。当泵达到正常转速后，再逐渐打开吐出管路上的闸阀，并调节到所需的工况。在吐出管上的闸阀关闭的情况下，泵连续工作的时间不能超过３分钟。

- 停止

- 逐渐关闭吐出管路上的闸阀，切断电源。

- 如环境温度低于０℃，应将泵内水放出，防止冻裂。

- 如长期停止使用，应将泵拆卸清洗上油，包装保管。

- 运转

- 在开车及运转过程中，必须注意观察仪表读数，轴承发热，填料漏水和发热及泵的噪音等是否正常，如果发现异常情况，应及时处理。

- 轴承温度最高不大于７５℃，并不得超过周围温度３５℃。

- 填料正常漏水应该是少量均匀的，每分钟约２０～３０滴。机械密封内径≤５０mm，泄漏量≤３ml/h，内径＞５０mm，泄漏量≤５ml/h。

- 轴承油位应保持在正常位置上，不能过高或过低，过低时应及时补充润滑油。

- 如密封环与叶轮配合部位的间隙磨损过大应更换新的密封环。

Starting, Running and Stopping

1 Starting

(1) Before assemble couplings, check the motor rotating direction, pump rotating is flexible. Fill lubricating oil inside cantilever support, oil level should be about in the center line of oil glass.

(2) Shut off fate valve on discharge pipe.

(3) Pour water into pump, or adopt vacuum pump to prime water.

(4) Switch on electric resource. When pump reach rate speed, slowly open the fate valve on discharge pipe. Adjust valve to reach required working condition. When the fate valve is shut off, the pump working time is not more than 3 minutes.

2 Stopping

(1) Slowly shut off the fate valve in discharge pipe, shut off electric resource.

(2) If the ambient temperature is low than 0℃, release water inside pump, to prevent the pump to frost crack.

(3) If the pump will stop for long time, the pump should be disassembled and cleaned, coasted oil, packed to protect well.

3 Running

(1) During running, must watch the date of instrument, the bearing temperature, too high packing leaking water, and overheated, and pump vibrate heavily, unexpected noise etc. if the condition is not normal, treat them in time.

(2) Max. bearing temperature is not more than 75℃, and not over 35℃ than ambient temperature.

(3) Packing leakage flow is 20~30 drops per minute. When mechanical seal diameter is ≤50mm, the leakage flow is ≤3ml/h; when mechanical seal diameter is ＞50mm, the leakage flow is ≤5ml/h.

(4) Bearing oil level should be in normal position, it can’t be too high or too low, when oil level is too low, the oil must be added.

(5) If wearing ring and impeller is worn out heavily, renew these parts.

订货须知

1、根据使用条件,正确选择性能参数(流量、扬程、吸程等)。

2、零件材料可根据用户要求选配,订货时需特别提出。

3、如果实际要求参数与性能表不符，公司可根据要求设计制造。

4、 本公司供货范围为泵、电机、公用底座、联轴器护罩及地脚螺栓，其它附件，如闸阀、止回阀、底阀、吐出锥管等，由用户选购。

Note

1. According to the user condition, select correct date (flow, head, NPSH etd.).

2. The material can supplied according to user requirment, it should be supplied in order specially.

3. If the required date have different with date in perfornance sheet, our company can design according to requirement.

4.The supply scope of the serial pump include pump, motor, .common base, coupling cover, foundation bolts, other accessories: fate valve, check valve, foot valve, discharge taper pipe etc. the user can select them to purchase.

故障、原因及其解决方法

| 故障 | 原因 | 解决方法 |
| --- | --- | --- |
| 1. 水泵不吸水，压力表及真空表的指针剧烈跳动。 | 注入水泵的水不够。水管或仪表漏气 | 再往水泵内注水或拧紧堵塞漏气处。 |
| 2. 水泵不吸水，真空表显示高度真空。 | 底阀没有打开或已淤塞。吸水管阻力太大。吸水管太高。 | 校正或更换底阀。清洗或更换吸水管。降低吸水高度。 |
| 3. 看压力表水泵出水处有压力，但水泵仍不出水。 | 出水管阻力太大。旋转方向不对。叶轮淤塞。水泵转速不够。 | 检查或缩短出水管。改变电机转向。清洗叶轮。检查电机或电压。 |
| 4. 流量低于预计 | 水泵淤塞。密封环磨损过多。转速不足。 | 清洗泵及管路。更换密封环。增加泵转速。 |
| 5. 水泵消耗的功率过大 | 填料压得太紧。叶轮磨损。水泵供水量增加。水泵轴与电机轴不在同一条中心线上。 | 调松压盖。更换叶轮。调节闸阀，降低流量。对准泵与电机中心线。 |
| 6. 水泵在工作过程中出现反常声音，流量下降，直到不出水。 | 闸阀开得太大。吸水管阻力过大。吸水高度过大。在吸水处有空气渗入，所输送液体温度过高。 | 调解闸阀降低流量。检查吸水管和底阀。减少吸水高度。拧紧或堵塞漏气处。降低液体温度。 |
| 7.轴承过热 | 没有油或油太脏。水泵轴与电机轴不在同一条中心线上。 | 注油或换油。对准泵与电机轴中心线。 |
| 8. 水泵震动 | 泵轴与电机轴不在同一条中心线上。轴承磨损。转子擦壳。基础松动。 | 对准泵和电机轴中心线。更换轴承。解体检查整台泵。加固基础。 |

Troubles & Causes & Remedies

| Troubles | Causes | Remedies |
| --- | --- | --- |
| 1. Pump loses prime and manometer pointers beats heavily. | The water poured in the pump is not enough, leakage of air from the pipe or instrument joints. | Pour water into pump again, block the leakage place. |
| 2. Pump loses prime but the vacuum gauge indicate a high vacuum degree | The foot valve is not open or it is plugged up. The resistance of suction is too high; the suction lift is too high | Correct or renew the foot valves, clean or renew the suction pipe. Make the suction head lower |
| 3. No water is pumped out, but high pressure is shown on the outlet manometer | The direction of rotation is not right. The discharge resistance is too high. Impeller flow passage is clogged | Change the rotating direction; check or shorten the pipe; clean the impeller |
| 4. Not enough flow | The impeller flow passage is clogged; the wearing ring is worn | Clean the impeller; renew the wearing ring |
| 5. Pump requires excessive power | Packing is too tight; the impeller is worn, excessive amount of flow | Loosen the packing gland; renew impeller; increase discharge pipe friction, reduce the flow |
| 6. Unexpected noise are heard and pump loses prime | Flow is too high; suction pipe friction is too big, suction height is too high; leakage of air found from the suction pipe; the temperature of liquid is too high | Increase discharge pipe friction to reduce flow; check suction pipe friction; check the foot valve; block the leaking place; make the temperature lower |
| 7.The bearing is overheated | The grease is not enough; the shaft running off-center | Add the grease. Correct the pump and motor shaft coaxial degree |
| 8. Pump vibrates heavily | The shaft running off-center | Correct the co-axial degree between pump and motor shaft |